DUPONT EXPERIMENTAL STATION WORK SUMMARY

Absorber #1

Pull a solution sample.  The unit has been on line for about a month.  I couldn’t pull a sample because Carrier is working on #6 and they needed all of the chillers running.

Absorber #2

Pull a solution sample. The Same reason as #1.  The unit has a filter installed. It seems tight but Wade had a leak he repaired on the heat exchanger.  This unit crystallized a couple of times when it was off.  I’ve asked the operators to shut the gate valves when they shut it down in case the automatic shut off is passing a little. If you get a chance you might want to check out the needle valve on this unit too it’s been a struggle to get a consistent steam input setting.

Absorber#3

Pull a solution sample. I pulled one and then they shut down for a month to fix the pipe so you better get another sample.   I think the tubes in the absorber and the condenser are scaled and that’s why we’re not able to get the tons out of this unit.

Absorber #4

Pull a solution sample. The same reason as #3.  They were having problem with condenser flow through this unit which limited the capacity.

Pumps

There is only one spare pump. I approached John Hostel a few weeks ago and he was receptive to getting spare pumps. They must have some money this year because they wouldn’t go for it a few years ago.

Contact Information

Contract Administrator

Raul Cozza

(302) 218 9898

Raul.j.cozza@dupont.com