## output-7.csv
Opened | Status | SR # | Customer PO# | Description | Non Billable Reason | SR Subtype | Last Labor Activity | Modified | Closed | Status | Substatus | Date Committed
2017-03-13 09:10 | Scheduled | 1-48030927221 |  | #10 Evap Waterbox Repair |  | Labor & Material | 2017-03-13 | 2017-03-13 09:10 |  | Scheduled | Tech Accepted | 2017-03-15 09:10
2017-03-08 15:16 | Scheduled | 1-47954372704 | 6501713698 | (6501713698) CHILLER #10 PRV SHAFT SEAL REPLACEMENT REPAIR OF THE FOLLOWING REFRIGERANT LEAK FOUND ON 03/03/17: COMPRESSOR PRE-ROTATION VANE SHAFT SEAL DISSMANTLE & REMOVE OLD SEAL ASSEMBLY FURNISH & INSTALL NEW SEAL ASSEMBLY WITH NEW ORINGS, GASKET, & FASTENERS PROPERLY SET & TORQUE SEAL VERFY TIGHTNESS WITH NITROGEN PRESSURE TEST ***COST OF REFRIGERANT RECOVERY & RECHARGING IS COVERED UNDER DUPONT PO#: 6501711947*** ***EVACUATION / DEHYDRATION WILL BE COVERED UNDER JCI QUOTE# 1-M0XUGZP*** |  | Custom Quote | 2017-03-10 | 2017-03-10 14:09 |  | Scheduled | Tech Accepted | 2017-03-10 15:16
2017-03-08 15:05 | Scheduled | 1-47953222455 | 6501713695 | (6501713695) CHILLER #10 REFRIGERANT PIPING LEAK REPAIR: REPAIR OF THE FOLLOWING LEAKS FOUND ON 03/03/17: 1-1/2" THREADED LIQUID REFRIGERANT TEE FEEDING OIL COOLER COMP. OIL RESERVOIR EQUALIZING LINE 1/4 THREADED FLARE ELBOW CUT & DISMANTLE REFRIGERANT LIQUID FEED PIPING & FITTINGS HAND THREAD 1/2" STEEL PIPING INSTALL NEW 1-1/2" THREADED TEE, BUSHINGS, STEEL FLARE ADAPTERS, & 3/4"OD FLARED STEEL TUBING VERIFY LEAK TIGHTNESS WITH NITROGEN PRESSURE TEST EVACUATE/ DEHYDRATE CHILLER & PERFORM VACUUM HOLD TEST ***COST OF REFRIGERANT RECOVERY & RECHARGING IS COVERED UNDER DUPONT PO#: 6501711947*** |  | Custom Quote | 2017-03-14 | 2017-03-10 14:08 |  | Scheduled | Tech Accepted | 2017-03-10 15:05
2017-03-06 07:55 | Scheduled | 1-47874641859 |  | E306 RTP Chilled Water Loop: Calculate appropriate System Fill Pressure based on height of highest coil and specific gravity of the Chilled Water. Isolate/Drain Expansion Tank. Increase Expansion Tank Bladder Pressure to System Fill Pressure with Nitrogen and Document. Set Glycol Feeder to System Fill Pressure and Engage. Manually Run Chilled Water Pumps in YORK RTP Chiller at various speeds with all Air Vents open. Increase Water Temperature as needed (w/assistance of DuPont) to facilitate air removal. Monitor process. When all air is removed, isolate air-vents required by DuPont, and re-open Expansion Tank to System. Train and Provide Literature as needed to DuPont Personnel. |  | Custom Quote |  | 2017-03-06 02:06 |  | Scheduled | Tech Accepted | 2017-03-08 07:55
2017-03-06 07:48 | Scheduled | 1-47873229676 | 6501711947 | (6501711947) CHILLER #10: Due to Refrigerant Leaks discovered on 03/03/2017 the following work is Recommended: Transfer entire R-134A charge to YORK Central Recovery Tank. Document weight of charge and calculated percentage loss based on design. Provide DuPont with documentation. Transfer recovered charge back into the Chiller after Leak Repair or DuPont's declining to repair. |  | Custom Quote | 2017-03-14 | 2017-03-08 12:41 |  | Scheduled | Tech On Site | 2017-03-08 07:48
2017-02-28 13:16 | Scheduled | 1-47444087633 |  | Chiller #9 Condenser tube plugging. |  | Labor & Material | 2017-02-28 | 2017-02-28 13:16 |  | Scheduled | Tech On Site | 2017-03-02 13:16
2017-02-28 12:52 | Scheduled | 1-47443336030 | 6501709952 | (6501709952) Chiller #10 Annual Maintenance 2017 Remove Refrigerant Sample for Chemical Analysis Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Furnish & Install Sight-Glass in Oil Return Line Change Compressor Oil w/ YORK J (Provided by DuPont) *IF REQUIRED* Disassemble Compressor Coupling and Check Cold Alignment Check Low-Speed Compressor Axial Thrust Reading Reassemble Coupling and Re-Check Compressor Coupling Cold Alignment Vacuum out Compressor Motor and Change Air Filters Change Oil in Compressor Motor Bearings (Provided by DuPont) Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Documents all tasks and Provide Comprehensive Report to DuPont |  | Custom Quote | 2017-03-08 | 2017-03-03 08:23 |  | Scheduled | Tech Accepted | 2017-03-02 12:52
2017-02-28 10:22 | Scheduled | 1-47436369564 | 6501697258 | (6501697258) CHILLER #9 EVAPORATOR WATERBOX REPAIRS: CLEAN AND PREPARE TUBE SHEET DIVISION PLATE TRACKING FOR STEEL EPOXY COATING APPLY BELZONA 1121 "SUPER XL-METAL" (PURCHASED UNDER DUPONT PO#: 6501690015) TO FILL IN PITS AND GOUGING CLEAN UP AND ENSURE EPOXY INTEGRITY AFTER 24HR CURE TIME SHAPE HARDENED EPOXY AS NEEDED PAINT ANY BARE STEEL ASSIST MDAVIS WITH INSTALLATION AND GASKETING OF REPAIRED DIVISION PLATE |  | Custom Quote | 2017-02-27 | 2017-03-10 12:47 |  | Scheduled | Tech Accepted | 2017-03-02 10:22
2017-02-27 12:09 | Scheduled | 1-47405246199 |  | (temporary holding spot for #9 Waterbox repair under PO 6501697258- NEED QUOTE) |  | Labor & Material |  | 2017-02-27 12:09 |  | Scheduled | Tech On Site | 2017-03-01 12:09
2017-02-27 12:02 | Scheduled | 1-47402231723 | 6501690015 | (EMERG. PO 6501690015) Order Goodway Brushes fro tube cleaning. |  | Labor & Material | 2017-02-27 | 2017-02-27 12:02 |  | Scheduled | Tech Accepted | 2017-03-01 12:02
2017-02-13 16:01 | Closed | 1-46720117811 | 6501701543 | 6501701543 CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4.975ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: TRANSFER REFRIGERANT CHARGE INTO CENTRAL RECOVERY TANK DOWN TO EPA SPECS BRING UP TO ATMOSPHERIC PRESSURE WITH SITE NITROGEN REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, O-RINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING EVACUATE CHILLER AND PERFORM VACUUM HOLD TEST TRANSFER REFRIGERANT CHARGE BACK INTO CHILLER |  | Custom Quote | 2017-02-28 | 2017-03-03 10:52 | 2017-03-03 10:52 | Closed | Closed | 2017-02-15 16:01
2017-02-13 15:55 | Open | 1-46718363513 |  | CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4.975ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: TRANSFER REFRIGERANT CHARGE INTO CENTRAL RECOVERY TANK DOWN TO EPA SPECS BRING UP TO ATMOSPHERIC PRESSURE WITH SITE NITROGEN REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, O-RINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING EVACUATE CHILLER AND PERFORM VACUUM HOLD TEST TRANSFER REFRIGERANT CHARGE BACK INTO CHILLER |  | Custom Quote |  | 2017-03-01 00:23 |  | Open | Unscheduled | 2017-02-15 15:55
2017-02-13 15:45 | Open | 1-46719052659 |  | CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4.975ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: TRANSFER REFRIGERANT CHARGE INTO CENTRAL RECOVERY TANK DOWN TO EPA SPECS BRING UP TO ATMOSPHERIC PRESSURE WITH SITE NITROGEN REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, O-RINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING EVACUATE CHILLER AND PERFORM VACUUM HOLD TEST TRANSFER REFRIGERANT CHARGE BACK INTO CHILLER |  | Custom Quote |  | 2017-03-01 00:23 |  | Open | Unscheduled | 2017-02-15 15:45
2017-02-10 20:07 | Closed | 1-46674736377 | 6501700807 | CHILLER # 7 OIL STOCK REPLENISHMENT: FURNISH QTY-6 5gal Pales of YORK "K" (30 Total Gallons) |  | Custom Quote | 2017-02-15 | 2017-02-21 12:36 | 2017-02-21 12:36 | Closed | Closed | 2017-02-12 20:07
2017-02-10 11:58 | Closed | 1-46661659154 | 6501690015 | Reset York Central Recovery tank scale to zero. |  | Labor & Material | 2017-02-10 | 2017-02-16 16:21 | 2017-02-16 16:20 | Closed | Closed | 2017-02-12 11:58
2017-02-09 11:17 | Closed | 1-46632636600 | 6501690015 | CHILLER #7 OIL LEVEL ADJUSTMENT: Drain and Measure Oil in Shaft Seal Oil Drainage Tank Calculated Shaft Seal Leakage for Last Year Add New YORK "K" Oil (Furnished by DuPont) to Compressor Sump to bring running level up into Top Sight Glass. *The Oil Level is currently running in the Lower Sight Glass. Chiller could shutdown on Low Oil Pressure* |  | Custom Quote | 2017-02-15 | 2017-02-21 13:20 | 2017-02-21 13:20 | Closed | Closed | 2017-02-11 11:17
2017-02-09 11:07 | Closed | 1-46632636274 | 6501700761 | 6501700761 Chiller #9 Annual Maintenance 2017 Remove Refrigerant Sample for Chemical Analysis Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Furnish & Install Sight-Glass in Oil Return Line Change Compressor Oil w/ YORK J (Provided by DuPont) Disassemble Compressor Coupling and Check Cold Alignment Check Low-Speed Compressor Axial Thrust Reading Reassemble Coupling and Re-Check Compressor Coupling Cold Alignment Vacuum out Compressor Motor and Change Air Filters Change Oil in Compressor Motor Bearings (Provided by DuPont) Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Documents all tasks and Provide Comprehensive Report to DuPont |  | Custom Quote | 2017-02-28 | 2017-03-03 12:02 | 2017-03-03 12:02 | Closed | Closed | 2017-02-11 11:07
2017-02-03 12:52 | Closed | 1-46491125544 | 6501697258 | (PO 6501697258) CHILLER #8 EVAPORATOR WATERBOX REPAIRS: CLEAN AND PREPARE TUBE SHEET FOR STEEL EPOXY COATING APPLY BELZONA 1121 "SUPER XL-METAL" (PURCHASED UNDER DUPONT PO#: 6501690015) TO FILL IN PITS AND GOUGING CLEAN UP AND ENSURE EPOXY INTEGRITY AFTER 24HR CURE TIME |  | Custom Quote | 2017-02-09 | 2017-02-21 12:52 | 2017-02-21 12:52 | Closed | Closed | 2017-02-05 12:52
2017-02-01 15:21 | Scheduled | 1-46438155392 | 6501695980 | CHILLER #10 EDDY-CURRENT EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR & CONDENSER TUBES (1,582 TOTAL) FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED UPON COMPLETION. *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED AND BRUSHED BEFORE TECHNICIAN ARRIVES. UNIT MUST BE READY FOR TESTING WITH NO WAITING TIME.* **THIS WORK IS CURRENTLY SCHEDULED FOR MARCH 9TH & 10TH. ACCESS TO SITE AND POWERHOUSE WILL NEED TO BE ARRANGED & PROVIDED FOR THE TECHNICIAN BY DUPONT** |  | Custom Quote | 2017-03-10 | 2017-02-01 09:26 |  | Scheduled | Tech Accepted | 2017-02-03 15:21
2017-02-01 15:01 | Closed | 1-46437169897 | 6501695977 | CHILLER #9 EDDY-CURRENT EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR & CONDENSER TUBES (1,582 TOTAL) FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED UPON COMPLETION. *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED AND BRUSHED BEFORE TECHNICIAN ARRIVES. UNIT MUST BE READY FOR TESTING WITH NO WAITING TIME.* **THIS WORK IS CURRENTLY SCHEDULED FOR FEB. 23RD & 24TH. ACCESS TO SITE AND POWERHOUSE WILL NEED TO BE ARRANGED & PROVIDED FOR THE TECHNICIAN BY DUPONT** |  | Custom Quote | 2017-02-24 | 2017-02-27 20:56 | 2017-02-27 20:56 | Closed | Closed | 2017-02-03 15:01
2017-01-30 14:41 | Closed | 1-46017866961 | 6501690015 | (Emergency PO) Chiller #8, erosion repair (pitting) to tube sheet in evaporator. |  | Labor & Material | 2017-01-31 | 2017-02-17 09:24 | 2017-02-17 09:24 | Closed | Closed | 2017-02-01 14:41
2017-01-27 11:44 | Closed | 1-45941594047 | 6501694234 | CHILLER #8 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#8 seal oil leak has been calculated at 4.92ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, O-RINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING **REFRIGERANT RECOVERY, EVACUATION, & RE-CHARGE IS COVERED UNDER OTHER QUOTES** |  | Custom Quote | 2017-02-02 | 2017-02-21 12:26 | 2017-02-21 12:26 | Closed | Closed | 2017-01-29 11:44
2017-01-27 11:29 | Cancelled | 1-45941194215 |  | CHILLER #8 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#8 seal oil leak has been calculated at 4.92ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, O-RINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING **REFRIGERANT RECOVERY, EVACUATION, & RE-CHARGE IS COVERED UNDER OTHER QUOTES** |  | Custom Quote |  | 2017-01-31 01:58 | 2017-01-27 14:12 | Cancelled | Created In Error | 2017-01-29 11:29
2017-01-26 08:13 | Closed | 1-45899325697 | 6501692933 | Chiller #8 Annual Maintenance 2017 Remove Refrigerant Sample for Chemical Analysis Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Change Compressor Oil w/ YORK J (Provided by DuPont) Disassemble Compressor Coupling and Check Cold Alignment Check Low-Speed Compressor Axial Thrust Reading Reassemble Coupling and Re-Check Compressor Coupling Cold Alignment Vacuum out Compressor Motor and Change Air Filters Change Oil in Compressor Motor Bearings (Provided by DuPont) Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Documents all tasks and Provide Comprehensive Report to DuPont *All other task, such as Recovery, Evacuation, Oil Sample, and Re-Charge are being performed under other Quotes* |  | Custom Quote | 2017-02-06 | 2017-02-21 12:27 | 2017-02-21 12:27 | Closed | Closed | 2017-01-28 08:13
2017-01-24 13:14 | Closed | 1-45848473572 | 6501691913 | YORK Centrifugal Chiller Annual Oil Analysis CHILLERS #7,#8,#9,#10: Remove Oil Samples from all YORK Centrifugals Send to Lab for Analysis Provide Analytical Reports w/ Recommendations for upcoming Annual Chiller Maintenance |  | Custom Quote | 2017-01-25 | 2017-01-26 15:36 | 2017-01-26 15:36 | Closed | Closed | 2017-01-26 13:14
2017-01-20 13:05 | Closed | 1-45765849262 | 6501691743 | CHILLER. #8 RELIEF TREE INSTALL Transfer Refrigerant to DuPonts Central Storage Tank according to EPA Specs. Record quantity recovered. Break Vacuum w/Nitrogen & Remove Current Relief Device. Install New 3-Way Valve, Relief Tree, and Relief Devices. Pressurize w/Nitrogen, Leak Test Entire Chiller. Evacuate Chiller & Perform Vacuum Hold Test. Recharge, Run, and Inspect Chiller Performance. ***DuPont will be responsible for providing all material to be installed and for constructing a scaffold that will allow the work to be carried out safely*** |  | Custom Quote | 2017-02-16 | 2017-02-17 11:02 | 2017-02-17 11:02 | Closed | Closed | 2017-01-22 13:05
2017-01-20 13:03 | Closed | 1-45765848899 | 6501691197 | CHILLER #8 EDDY-CURRENT EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR & CONDENSER TUBES (1,582 TOTAL). FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED UPON COMPLETION. *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED AND BRUSHED BEFORE TECHNICIAN ARRIVES. UNIT MUST BE READY FOR TESTING WITH NO WAITING TIME.* **THIS WORK IS CURRENTLY SCHEDULED FOR JAN. 27TH & 28TH. ACCESS TO SITE AND POWERHOUSE WILL NEED TO BE ARRANGED & PROVIDED FOR THE TECHNICIAN BY DUPONT ON SATURDAY THE 28TH.** |  | Custom Quote | 2017-01-27 | 2017-01-31 18:10 | 2017-01-31 18:10 | Closed | Closed | 2017-01-22 13:03
2017-01-19 13:38 | Closed | 1-45734478692 | 6501690015 | Consultive service of 1/18. Emergency work of 1/19. |  | Labor & Material | 2017-01-19 | 2017-01-26 13:10 | 2017-01-26 13:10 | Closed | Closed | 2017-01-21 13:38
2017-01-17 14:26 | Closed | 1-45677647587 | 6501690015 | CHILLER #8 LOW OIL LEVEL Add appropriate amount of YORK "J" Oil (Customer Supplied) to Chiller #8 to bring back to Normal Operating Level. Measure Seal Oil Leakage and Calculate Leak rates on #8,9,&10 to determine Condition of Shaft Seals. Make necessary Adjustments on Chiller #8's Vane Arm Assembly. Change and Tighten Fasteners. Apply Sealant to Actuator Motor Shaft. |  | Custom Quote | 2016-12-28 | 2017-01-26 14:09 | 2017-01-26 14:09 | Closed | Closed | 2017-01-19 14:26
2017-01-09 16:22 | Closed | 1-45487366293 | 6501690015 | Scheduling/consultive: Ruptured Disc replacements on qty 4 absorber chillers |  | Labor & Material | 2017-01-10 | 2017-01-26 13:11 | 2017-01-26 13:11 | Closed | Closed | 2017-01-11 16:22
2016-12-28 15:02 | Scheduled | 1-43713008400 |  | RUPTURED DISC REPAIR - MOVING TO QUOTE 1-K2OOT6G WHEN RAUL GETS PO. Temporary holding spot for Mr. Kevin Fraze. | Non billable SR | Customer Satisfaction |  | 2017-01-07 12:41 |  | Scheduled | Tech Accepted | 2016-12-30 15:02
2016-11-16 11:36 | Closed | 1-42462980933 | 6501663924 | CHILLERS #8, #9, #10 SOFTWARE UPGRADE: Coordinate with DuPont Operators to Shutdown and Lockout one Chiller at a time UPGRADE all three CHILLER MICROBOARDs to the LATEST Revision of CONTROL LOGIC SOFTWARE (v. C.03F.03) Unlock, Start Up, and Verify CHILLER Control Operation, and Ensure proper Communication with MICROGATEWAY Modbus Interface Chillers #8 and #9 are currently running with the Original Software C.03F.00 Chiller #10 is currently running Software Version C.03F.01 |  | Custom Quote | 2016-11-29 | 2016-11-30 15:00 | 2016-11-30 15:00 | Closed | Closed | 2016-11-18 11:36
2016-10-26 15:42 | Closed | 1-41561145038 | 6501611952 | ABSORBERS #2 & #3 PROVIDE MATERIAL: LITHIUM MOLYBDATE INHIBITOR based on recent SOLUTION Analysis to bring Levels back to Optimal. *Inhibitor levels in ABSORBERS #1 & #4 are within the Normal range and do not need adjustment at this time.* |  | Custom Quote |  | 2016-11-08 15:40 | 2016-11-08 15:40 | Closed | Closed | 2016-10-28 15:42
2016-10-25 13:51 | Cancelled | 1-41528738833 |  | Material associated with PM - customer to supply. |  | Labor & Material |  | 2016-12-19 19:18 | 2016-12-19 19:18 | Cancelled | Customer Cancelled | 2016-10-27 13:51
2016-09-29 07:40 | Closed | 1-40855334427 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2016-11-01 | 2016-12-09 09:02 | 2016-12-09 09:02 | Closed | Closed | 2016-10-01 07:40
2016-09-16 14:24 | Closed | 1-38992535910 | 6501638582 | Chiller #9 Fault; transducer issue |  | Labor & Material | 2016-09-19 | 2016-09-20 14:42 | 2016-09-20 14:42 | Closed | Closed | 2016-09-18 14:24
2016-08-25 11:03 | Closed | 1-37498214070 | 6501630558 | ABSORBER #1 "AUTO-PURGE FAILURE" Troubleshooting, Leak Test & Repairs: Completely DISASSEMBLE Purge Header REMOVE and REPLACE Faulty Solenoid Valve (1SOL) CLEAN all PIPING and THREADS DISASSEMBLE Automatic Ball Valve (2SOL) CLEAN and Re-Assemble RE-ASSEMBLE all PIPING w/ New Sealant and Flange Gasket. REPLACE PURGE CHECK VALVE and TRANSDUCER PRESSURIZE Purge Header and Verify that it is Leak Free and Dry Return Auto-Purge Operation to "AUTOMATIC" |  | Custom Quote | 2016-08-25 | 2016-08-29 12:49 | 2016-08-29 12:49 | Closed | Closed | 2016-08-27 11:03
2016-08-22 14:09 | Cancelled | 1-37410017994 |  | Absorber #1; Auto Purge Failure. Trouble shooting, leak test and repair. |  | Labor & Material |  | 2016-12-19 18:11 | 2016-12-19 18:11 | Cancelled | Customer Cancelled | 2016-08-24 14:09
2016-08-03 12:07 | Closed | 1-36853244088 | 6501620987 | ABSORBER #3 Due to the HIGH FREQUENCY of PURGES while Operational, along with CHEMICAL ANALYSIS, Recommend INSTALLING LITHIUM NITRATE TYPE INHIBITOR Perform LEAK TEST of PURGE TREE HEADER and REPAIR any LEAKS FOUND ABSORBER #3 should REMAIN OPERATING in order to properly TREND PURGE FREQUENCY, and determine if there are other possible causes |  | Custom Quote | 2016-08-11 | 2016-08-26 09:51 | 2016-08-26 09:51 | Closed | Closed | 2016-08-05 12:07
2016-08-01 14:20 | Closed | 1-36780001028 | 6501620268 | Chris Cooper requested installation of relief device on central recovery liquid line. |  | Labor & Material | 2016-08-02 | 2016-08-26 13:08 | 2016-08-26 13:08 | Closed | Closed | 2016-08-03 14:20
2016-07-26 07:48 | Closed | 1-36516053617 | 6501620268 | Due to weather event, Chillers #8 and 9 will not restart- power failure. Troubleshoot and repair. |  | Labor & Material | 2016-07-27 | 2016-08-02 10:52 | 2016-08-02 10:52 | Closed | Closed | 2016-07-28 07:48
2016-07-20 13:54 | Closed | 1-36363184896 | 6501616658 | ABSORBER #1 Due to High Concentration of Suspended Solids after Solution Pump Failure, FILTERING is REQUIRED RELOCATE Canister from ABS#2 to ABS#3 INSTALL NEW HOSES, FLANGE and BALL VALVE (on VP7) FURNISH 18 New PALL Bromide Solution FILTERS to REPLENISH Supply onsite. (6 Filters per Changeout) REMOVE and REPLACE current clogged Filters CLEAN out Canister EVACUATE and RETURN to Service REPLACE FILTERS as needed until SUSPENDED SOLIDS in SOLUTION is at ACCEPTABLE LEVELS |  | Custom Quote | 2016-07-22 | 2016-08-31 08:11 | 2016-08-31 08:11 | Closed | Closed | 2016-07-22 13:54
2016-07-08 14:33 | Pending Adjustment | 1-36028109391 | Raul Cozza | ABSORBER #2 FURNISH 18 New PALL Bromide Solution FILTERS to REPLENISH Supply onsite. (6 Filters per Changeout) REMOVE and REPLACE current clogged Filters CLEAN out Canister EVACUATE and RETURN to Service |  | Custom Quote | 2016-07-21 | 2016-08-30 06:51 |  | Pending Adjustment | Pending Adjustment | 2016-07-10 14:33
2016-07-07 11:09 | Closed | 1-35974893871 | 6501611959 | ABSORBER #3 REMOVE and REPLACE Faulty Solenoid Valve (1SOL) CLEAN Purge Header Return Purge Operation back to AUTOMATIC OPERATORS will no longer need to worry about MANUALLY Purging PURGE TANK |  | Custom Quote | 2016-07-07 | 2016-07-22 10:06 | 2016-07-22 10:06 | Closed | Closed | 2016-07-09 11:09
2016-07-06 11:16 | Closed | 1-35942212834 | 6501611952 | ABSORBERS #2, #3, #4 LITHIUM MOLYBDATE INHIBITOR based on recent SOLUTION Analysis to bring Levels back to Optimal. |  | Custom Quote | 2016-07-06 | 2016-07-22 10:14 | 2016-07-22 10:14 | Closed | Closed | 2016-07-08 11:16
2016-07-05 11:20 | Closed | 1-35911259064 | 6501611969 | ABSORBER #1 Furnish NEW Motor Assembly for the Main Solution Pump (This is the entire Pump with exception on the Volute and Impeller) ** The cost of installing the Pump and all Labor associated with bringing ABSORBER #1 back online will be covered by the original JCI Quote # 1-G8EH8ER. ** ** For the price of both Quotes, DuPont will have 1 NEW Solution Pump w/Motor Installed & 1 Rebuilt Solution Pump w/Motor, left onsite as a Spare ** **** Lead Time for the NEW Motor Assembly from the Factory is currently 3 Weeks **** |  | Custom Quote | 2016-07-08 | 2016-07-22 09:59 | 2016-07-22 09:59 | Closed | Closed | 2016-07-07 11:20
2016-07-01 14:04 | Closed | 1-35841204337 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2016-08-18 | 2016-08-29 11:04 | 2016-08-29 11:04 | Closed | Closed | 2016-07-03 14:04
2016-06-23 12:48 | Closed | 1-35376456584 |  | Per Chris Cooper: Removal and re-installation of Central SUVA Storage Tank Liquid Line Relief valve 315XRV00219XXX for testing. |  | Labor & Material | 2016-06-23 | 2016-06-30 11:56 | 2016-06-30 11:56 | Closed | Closed | 2016-06-25 12:48
2016-06-23 12:42 | Closed | 1-35376456034 | 6501608975 | ABSORBER #1 Remove and Replace Main Solution Pump Wearing Rings Remove and Replace Seized Studs in Pump Casing Thoroughly Clean all Pump Parts Furnish and Install New Pump Motor Carbon Graphite Bearings Re-Assemble Pump with Original Impeller Re-Install Pump with New Casing Gasket Install new Motor Contactor and Overload Assembly and Re-wire the pump Remove and Replace Fouled Sight-glasses in Absorber Section Evacuate Absorber Re-Install removed Solution through Filters Reset Valves to Original Positions Startup and Purge Absorber Ensure proper Operation |  | Custom Quote | 2016-07-28 | 2016-07-29 08:50 | 2016-07-29 08:50 | Closed | Closed | 2016-06-25 12:42
2016-06-20 13:07 | Closed | 1-35270891278 | 6501605952 | ABSORBER #1 Machining will be performed on the Main Solution Pump Rotor Assembly to repair worn parts and return to design specs. Have Impeller Balance verified. (If unbalanced an additional quote will be provided). |  | Custom Quote | 2016-06-27 | 2016-06-30 18:55 | 2016-06-30 18:55 | Closed | Closed | 2016-06-22 13:07
2016-06-09 07:10 | Closed | 1-34850489163 | 6501600380 PO attached | ABSORBER#1 MAIN SOLUTION PUMP INSPECTION Transfer Solution to Generators and Drums Disconnect and Pull Main Solution Pump Inspect, Clean out Solution, Disassemble Pump Inspect Bearings, Impeller, and Pump Seals Install Blank on Pump Volute until Additional Repairs are made |  | Custom Quote | 2016-06-17 | 2016-06-20 10:15 | 2016-06-20 10:15 | Closed | Closed | 2016-06-11 07:10
2016-06-05 19:11 | Closed | 1-34691988271 | 6501598682 | Inspect and Repair Chiller #8 Evaporator issues, ESL Powerhouse (E315) |  | Labor & Material | 2016-06-23 | 2016-06-24 21:08 | 2016-06-24 21:08 | Closed | Closed | 2016-06-07 19:11
2016-06-01 10:00 | Closed | 1-34566790831 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2016-07-19 | 2016-08-10 11:43 | 2016-08-10 11:43 | Closed | Closed | 2016-06-03 10:00
2016-05-27 13:19 | Closed | 1-34404994575 | Diane Skilton | Chiller #10, not loading. |  | Labor & Material | 2016-05-27 | 2016-06-25 07:34 | 2016-06-25 07:34 | Closed | Closed | 2016-05-29 13:19
2016-05-25 07:11 | Closed | 1-34287950346 |  | Abs #4; high solution concentration. KF |  | Labor & Material | 2016-05-25 | 2016-05-31 14:02 | 2016-05-31 09:09 | Closed | Closed | 2016-05-27 07:11
2016-05-13 15:29 | Closed | 1-33993104959 | 6501590122 | repair limit switch on chiller#10 |  | Labor & Material | 2016-05-13 | 2016-05-27 16:44 | 2016-05-27 16:43 | Closed | Closed | 2016-05-15 15:29
2016-05-13 11:14 | Closed | 1-33983397168 |  | -replace relief devices on chiller#7 -additional Rupture Disk Replacement on Chiller #7 and its Central Storage tank. |  | Labor & Material | 2016-05-16 | 2016-05-31 16:20 | 2016-05-31 16:20 | Closed | Closed | 2016-05-15 11:14
2016-05-01 09:34 | Closed | 1-33644815808 |  | Preventive Maintenance Absorber #1 has been under repair. Unable to perform PM. | Non billable SR | Scheduled Service | 2016-07-18 | 2016-07-30 12:00 | 2016-07-30 12:00 | Closed | Closed | 2016-05-03 09:34
2016-04-21 14:17 | Closed | 1-33069099287 | 6501580874 | ROOFTOP CHILLER E336 SERVICE SCHEDULED FOR 4/30 RUSSELL YETTER CONTACT JIM TIDWELL-302.218.9528 |  | Labor & Material | 2016-04-30 | 2016-06-10 11:53 | 2016-06-10 11:53 | Closed | Closed | 2016-04-23 14:17
2016-04-05 08:38 | Closed | 1-32345011806 |  | Chiller #7 - Troubleshoot Oil Separator |  | Labor & Material | 2016-04-05 | 2016-04-14 12:23 | 2016-04-14 12:23 | Closed | Closed | 2016-04-07 08:38
2016-04-01 10:58 | Closed | 1-32243121739 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2016-05-18 | 2017-01-06 09:47 | 2017-01-06 09:47 | Closed | Closed | 2016-04-03 10:58
2016-03-30 14:17 | Cancelled | 1-32160999861 |  | Chiller #7 Startup - Trailing cost against Maintenance SR | Non billable SR | Customer Satisfaction |  | 2016-04-14 08:54 | 2016-04-14 08:54 | Cancelled | Created In Error | 2016-04-01 14:17
2016-03-07 14:18 | Closed | 1-31515692746 | 6501560949 | Chiller #7 - Leak Repair |  | Labor & Material | 2016-03-10 | 2016-03-18 14:56 | 2016-03-18 14:56 | Closed | Closed | 2016-03-09 14:18
2016-02-22 09:28 | Closed | 1-30777898703 | 6501537255 | Chiller 7 (ESL E315) - Labor continuation (Rupture disks) |  | Labor & Material | 2016-02-24 | 2016-03-11 19:16 | 2016-02-26 19:59 | Closed | Closed | 2016-02-24 09:28
2016-02-12 08:45 | Closed | 1-29274542300 | 6501549099 | Remove samples of compressor oil and refrigerant for chemical analysis. Refrigerant leak test chiller and document leaks found (repair “minor” leaks, if possible). Transfer R-134A to storage tank for accurate weight of charge (Leaving 5psi on Chiller). Furnish and change compressor oil filters, and all driers. Furnish and change gearbox oil filters and oil (*Gear/Motor Oil furnished by DuPont*). Inspect gears and internal gearbox components. Disassemble motor coupling and check cold alignment. Repack motor coupling with grease and reassemble. Disassemble Compressor coupling. Check compressor axial thrust readings. Check compressor coupling cold alignment. Reassemble coupling. Vacuum out compressor motor. Brush clean all oil cooler tubes (Gear & Compressor). Transfer R-134A charge back into Chiller. |  | Custom Quote | 2016-03-31 | 2016-04-14 08:53 | 2016-04-14 08:53 | Closed | Closed | 2016-02-14 08:45
2016-02-10 15:54 | Closed | 1-29228476787 | 6501537255 | Chiller 7 (ESL E315) - Labor continuation |  | Labor & Material | 2016-02-12 | 2016-02-16 14:27 | 2016-02-16 14:27 | Closed | Closed | 2016-02-12 15:54
2016-02-04 14:12 | Closed | 1-29066059613 | 6501545663 | Eddy-Current Testing performed on all Evaporator (1852) and Condenser (2590) Tubes. Detailed report of analysis will be provided to DuPont. Water Box Heads must be removed, all tubes thoroughly cleaned, and scaffolding set up, before technician arrives |  | Custom Quote | 2016-03-01 | 2016-03-09 09:07 | 2016-03-09 09:07 | Closed | Closed | 2016-02-06 14:12
2016-02-02 12:48 | Closed | 1-28998918974 | 6501541957 | Complete replacement of faulty and obsolete Compressor Pneumatic Vane Actuator w/ integral Pilot Positioner. (The new actuator is the latest model of its kind, thereby making replacements parts readily available in the future.) Replace control air pressure throttling valve. Replace any pneumatic tubing or fittings necessary. Replace pneumatic air filters on for control air and main piston air. Set pressure regulators to design pressures. Set up correct position stroke length and span. Calibrate controls for proper Vane positioning and stable control of Compressor. Check control and operation of both Interstage and Hot Gas Bypass Bypass valves. Ensure that the are working as per design and in conjunction with Vane Actuator. |  | Custom Quote | 2016-03-18 | 2016-03-29 12:54 | 2016-03-29 12:53 | Closed | Closed | 2016-02-04 12:48
2016-01-29 10:33 | Closed | 1-28882156385 | 6501537255 | Chiller 7 (ESL E315) - Labor continuation |  | Labor & Material | 2016-02-01 | 2016-07-12 19:25 | 2016-02-05 08:29 | Closed | Closed | 2016-01-31 10:33
2016-01-21 13:41 | Closed | 1-28657093467 | 6501537307 | Furnish qty-4 rolls of gasket material p/n 028-03242-050. Shipping included. |  | Custom Quote |  | 2016-01-25 13:46 | 2016-01-25 13:46 | Closed | Closed | 2016-01-23 13:41
2016-01-18 20:57 | Closed | 1-28577700955 | 6501537148 | CHILLER #7 Capacity Control Inspection, Diagnosis, and Evaluation of any Repairs Necessary. - This work is in response to DuPont Powerhouse Operators reporting erratic operation of Chiller #7's Capacity Control Pre-Rotation Vanes and a Vibration Shutdown Fault. - If substantial repairs are determined to be necessary, a separate quote will be provided to cover the additional Labor and Materials involved. |  | Custom Quote | 2016-01-20 | 2016-01-25 17:38 | 2016-01-25 17:38 | Closed | Closed | 2016-01-20 20:57
2016-01-18 13:05 | Closed | 1-28571115916 | 6501537255 | Due:1/18 Desc:Chiller #7, evaluate replacement of rupture discs. Svc Hrs:N/A Access:N/A Contact:Raul Cozza 302-695-7842 Caller:JCI mech Kevin Fraze 302-353-0315 |  | Labor & Material | 2016-01-29 | 2016-02-01 16:24 | 2016-02-01 16:24 | Closed | Closed
2016-01-12 15:13 | Cancelled | 1-28429060770 |  | Chiller #7 - Look over vanes control |  | Labor & Material |  | 2016-02-11 10:34 | 2016-02-11 10:34 | Cancelled | Created In Error | 2016-01-14 15:13
2015-11-05 08:43 | Closed | 1-26693184827 | 6501505894 | Molybdate Corrosion Inhibitor in quantities specified by recent Lithium Bromide lab analysis for each ABSORBER. *This quote is for MATERIAL ONLY. Labor for adding Inhibitor will be covered under the current Maintenance Contract.* |  | Custom Quote |  | 2015-11-10 16:57 | 2015-11-10 16:57 | Closed | Closed | 2015-11-07 08:43
2015-10-30 13:08 | Closed | 1-26526940839 |  | Replace defective Purge Solenoid Valves (1SOL) on ABSORBER #1 and ABSORBER #2. Current valves were not properly sealing when closed, causing the Absorber Logic Board to cease "Smart" Auto-Purge Operation, and requiring Operators to Manually purge the Purge Tank while in Absorbers are in operation. Return Purges to Auto-Mode and Inspect Operation. **Quote DOES NOT include the price of the New Solenoid Valves. These were already purchased and billed to DuPont on a previous job.** |  | Custom Quote | 2015-10-30 | 2015-11-02 12:47 | 2015-11-02 12:47 | Closed | Closed | 2015-11-01 13:08
2015-10-03 06:05 | Closed | 1-25700650894 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2015-11-16 | 2015-12-29 14:10 | 2015-12-29 14:10 | Closed | Closed | 2015-10-05 06:05
2015-09-24 07:51 | Closed | 1-25343174313 | 6501485253 | Furnish qty-12 York Oil Filters p/n 025-11225-000 Shipping included |  | Custom Quote |  | 2015-10-01 18:34 | 2015-10-01 18:34 | Closed | Closed | 2015-09-26 07:51
2015-09-14 10:59 | Closed | 1-25030777306 |  | ABS#1 - Troubleshoot Smart Purge Repair |  | Labor & Material | 2015-09-18 | 2015-10-03 19:08 | 2015-09-26 13:01 | Closed | Closed | 2015-09-16 10:59
2015-09-14 10:56 | Closed | 1-25030508963 | Raul Cozza | ABS#4 - Troubleshoot main solution pump. |  | Labor & Material | 2015-09-15 | 2015-09-26 14:02 | 2015-09-26 12:43 | Closed | Closed | 2015-09-16 10:56
2015-09-08 13:37 | Closed | 1-24856075192 |  | Absorber #2 in alarm |  | Labor & Material | 2015-09-15 | 2016-02-10 19:18 | 2015-09-26 12:38 | Closed | Closed | 2015-09-10 13:37
2015-08-19 12:23 | Closed | 1-24241567558 | 6501469316 | Troubleshoot issue with ABS#4 – Motor tripping off on overloads - ABS#4 Refrig Pump Motor Removal, Rebuild and Replacement with new motor. |  | Labor & Material | 2015-08-27 | 2015-08-31 13:53 | 2015-08-31 13:52 | Closed | Closed | 2015-08-21 12:23
2015-08-17 16:12 | Closed | 1-24187391580 | 6501469316 | YORK Parts ONLY for ABSORBER #4 (All Parts are New and should be Replaced when Motor/Rotor/Impeller Assembly is pulled): Refrigerant Pump Motor Motor Front and Rear Bearings Pump Casing Wearing Ring Motor Side Wearing Ring Impeller Fastening Hardware Pump Casing Gasket Motor Contactor & Overload Assembly All parts are available at are Baltimore Parts Center in Limited Quantities. |  | Custom Quote |  | 2015-10-05 15:24 | 2015-10-05 15:23 | Closed | Closed | 2015-08-19 16:12
2015-08-17 10:49 | Closed | 1-24173921374 | 6501524856 | Chiller 8 - Troubleshoot PVR issue |  | Labor & Material | 2015-08-19 | 2016-01-28 16:12 | 2016-01-28 16:02 | Closed | Closed | 2015-08-19 10:49
2015-08-05 14:52 | Closed | 1-23822214702 | 6501469316 | Troubleshoot Absorber Ref. Pump #4. |  | Labor & Material | 2015-08-10 | 2015-08-21 18:26 | 2015-08-21 18:26 | Closed | Closed | 2015-08-07 14:52
2015-06-11 09:54 | Closed | 1-22014279916 | 6501441353 | Defective auto purge actuator. |  | Labor & Material | 2015-06-12 | 2015-06-30 08:18 | 2015-06-30 08:18 | Closed | Closed | 2015-06-13 09:54
2015-06-05 10:26 | Closed | 1-21813419439 |  | Building 336 - Troubleshoot chiller operation |  | Labor & Material | 2015-06-20 | 2015-06-30 10:08 | 2015-06-30 10:08 | Closed | Closed | 2015-06-07 10:26
2015-06-02 10:34 | Closed | 1-21689841312 | 6501455439 | Chiller #9 - Oil leak |  | Labor & Material | 2015-06-02 | 2015-08-03 13:58 | 2015-08-03 13:58 | Closed | Closed | 2015-06-04 10:34
2015-05-07 09:38 | Closed | 1-20800016829 | 6501434411 | Panel for Aborsober #1 blew out. |  | Labor & Material | 2015-05-18 | 2015-07-10 13:15 | 2015-07-10 13:15 | Closed | Closed | 2015-05-09 09:38
2015-05-07 09:00 | Closed | 1-20798887284 | 6501426534 | Furnish qty-1 55 gallon drum of new York "K" oil. Shipping included. |  | Custom Quote |  | 2015-05-26 14:12 | 2015-05-26 14:12 | Closed | Closed | 2015-05-09 09:00
2015-05-06 13:35 | Closed | 1-20772877187 | 6501426354 | Supply 36 Solution filters for Absorber #2. |  | Custom Quote |  | 2015-05-27 14:12 | 2015-05-27 14:12 | Closed | Closed | 2015-05-08 13:35
2015-04-14 13:16 | Closed | 1-20136654284 | LOX612634 | Chiller #7 low oil pressure |  | Labor & Material | 2015-04-14 | 2015-04-17 12:03 | 2015-04-17 12:03 | Closed | Closed | 2015-04-16 13:16
2015-04-01 09:14 | Closed | 1-19763475372 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2015-05-08 | 2015-05-30 10:21 | 2015-05-30 10:21 | Closed | Closed | 2015-04-03 09:14
2015-03-01 08:14 | Closed | 1-18893440282 |  | Preventive Maintenance | Non billable SR | Scheduled Service |  | 2015-05-31 22:12 | 2015-05-31 22:12 | Closed | Closed | 2015-03-03 08:14
2015-02-06 09:39 | Closed | 1-18202458640 | LOX611091 | Furnish and install qty-1 new compressor shaft seal on Chiller #7. m/n OM3000 s/n MRP626904 Lock out / Tag out all energy sources Recover refrigerant into chiller reciever Disconnect coupling between gearbox and compressor Check and record compressor alignment readings Check and record compressor axial thrust reading Install new compressor shaft seal Reassemble compressor coupling Pressure test and evacuate chiller Recharge chiller with recovered refrigerant Exclusions: Additional refrigerant charge if needed Leak repairs other than compressor shaft seal |  | Custom Quote | 2015-02-25 | 2015-03-20 08:54 | 2015-03-20 08:54 | Closed | Closed | 2015-02-08 09:39
2015-01-23 15:32 | Closed | 1-17767611385 | LOX610743 | Material Only - Provide (6) 392 10719 000 KIT, FILTER and (6) 028 08312 001 KIT, REPL GASKETS |  | Custom Quote |  | 2015-01-30 19:45 | 2015-01-30 19:45 | Closed | Closed | 2015-01-25 15:32
2015-01-16 08:49 | Closed | 1-17578850663 | LOX610534 | Furnish and install qty-4 new transducers and qty-8 new temperature sensors on Chiller #9. Connect all wiring and verify operation of each device. |  | Custom Quote | 2015-01-22 | 2015-04-09 08:46 | 2015-04-09 08:44 | Closed | Closed | 2015-01-18 08:49
2015-01-01 10:54 | Closed | 1-17237691041 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2015-03-20 | 2015-05-31 22:15 | 2015-05-31 22:15 | Closed | Closed | 2015-01-03 10:54
2014-12-10 13:06 | Closed | 1-16741327980 | LOX609895 | Furnish gasket material for York Absorption chillers. qty-300 ft of Bulb gasket material qty-25 ft of baffle gasket material |  | Custom Quote |  | 2014-12-17 14:19 | 2014-12-17 14:19 | Closed | Closed | 2014-12-12 13:06
2014-11-01 11:59 | Closed | 1-15599227365 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2015-06-22 | 2016-03-10 14:46 | 2016-03-10 14:46 | Closed | Closed | 2014-11-03 11:59
2014-10-31 14:42 | Closed | 1-15566817791 |  | Rebuild compressor on Chiller #9. m/n OTT4G2-ZBES s/n GACM117864 Lock out / tag out all energy sources Recover and store all refrigerant using plant recovery system Disconnect compressor coupling Disconnect all compressor piping Set up rigging and lower compressor to ground Record compressor thrust and runout readings Disassemble entire compressor and evaluate all parts Furnish and install new compressor bearings and gaskets Record compressor thrust and runout readings after rebuild Rig compressor onto chiller Reconnect all piping Pressure test system with nitrogen and leak test Check and adjust motor alignment as needed Reassemble compressor coupling Evacuate system and charge with recovered refrigerant Run chiller and check operation Provide all documentation Note: Pricing per chiller. | Non billable SR | Shared Resource to Projects | 2015-01-30 | 2015-08-18 08:09 | 2015-08-18 08:09 | Closed | Closed | 2014-11-02 14:42
2014-10-15 14:41 | Cancelled | 1-15113570309 | LOX608154 | Rebuild compressor on Chiller #9. m/n OTT4G2-ZBES s/n GACM117864 Lock out / tag out all energy sources Recover and store all refrigerant using plant recovery system Disconnect compressor coupling Disconnect all compressor piping Set up rigging and lower compressor to ground Record compressor thrust and runout readings Disassemble entire compressor and evaluate all parts Furnish and install new compressor bearings and gaskets Record compressor thrust and runout readings after rebuild Rig compressor onto chiller Reconnect all piping Pressure test system with nitrogen and leak test Check and adjust motor alignment as needed Reassemble compressor coupling Evacuate system and charge with recovered refrigerant Run chiller and check operation Provide all documentation Note: Pricing per chiller. |  | Custom Quote |  | 2015-01-23 12:20 | 2015-01-23 12:20 | Cancelled | Created In Error | 2014-10-17 14:41
2014-10-15 14:20 | Closed | 1-15112969639 | LOX608468 | Parts only. Provide Two Three way Valves for the installation of dual relief valves on Chiller #8 and #9 |  | Custom Quote |  | 2014-11-13 10:58 | 2014-11-13 10:58 | Closed | Closed | 2014-10-17 14:20
2014-10-15 14:14 | Closed | 1-15112209612 | LOX608467 | Provide Corrosion Inhibitor for the Absorption Chillers Per the Solution Analysis. Provide the labor to charge the inhibitor into the Absorbers. |  | Custom Quote | 2014-10-31 | 2014-11-04 10:54 | 2014-11-04 10:54 | Closed | Closed | 2014-10-17 14:14
2014-10-08 06:05 | Closed | 1-14907457363 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2014-11-04 | 2014-11-29 13:05 | 2014-11-29 13:05 | Closed | Closed | 2014-10-10 06:05
2014-10-07 13:34 | Cancelled | 1-14883658051 |  | Pressurize the absorbers |  | Labor & Material |  | 2015-01-16 10:16 | 2015-01-16 10:16 | Cancelled | Created In Error | 2014-10-09 13:34
2014-08-08 17:52 | Closed | 1-13001254857 | LOX606511 | De-crystalize ABS #2 in the powerhouse (PO Req##68377) |  | Labor & Material | 2014-08-19 | 2014-08-29 09:14 | 2014-08-29 09:14 | Closed | Closed | 2014-08-10 17:52
2014-07-02 16:12 | Closed | 1-11975635560 | LGGC22452 | Troubleshoot the E336 Chiller |  | Labor & Material | 2014-07-02 | 2014-08-21 15:48 | 2014-08-21 15:48 | Closed | Closed | 2014-07-04 16:12
2014-07-01 09:09 | Closed | 1-11933135666 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2014-08-20 | 2014-08-30 02:08 | 2014-08-30 02:08 | Closed | Closed | 2014-07-03 09:09
2014-06-30 15:36 | Closed | 1-11907374430 | LOX606606 | Chiller #7 oil leak |  | Labor & Material | 2014-07-02 | 2014-08-18 08:11 | 2014-08-18 08:11 | Closed | Closed | 2014-07-02 15:36
2014-06-27 08:16 | Closed | 1-11825182709 | LOX606593 | Absorber #4 - Solution pump tripped on overload. |  | Labor & Material | 2014-06-27 | 2014-08-14 16:15 | 2014-08-14 16:14 | Closed | Closed | 2014-06-29 08:16
2014-06-25 15:03 | Closed | 1-11773195658 | LOX605366 | Absorber #2 crystallized. Steam shut off valvle is passing |  | Labor & Material | 2014-06-25 | 2014-08-14 08:36 | 2014-08-14 08:36 | Closed | Closed | 2014-06-27 15:03
2014-04-01 08:28 | Closed | 1-9803714643 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2014-06-24 | 2014-08-30 00:31 | 2014-08-30 00:30 | Closed | Closed | 2014-04-03 08:28
2014-03-26 11:19 | Closed | 1-9687624328 | LOX597574 | INCLUDED • Disassemble and remove existing Pin Relief Valve. • Provide and install a 3 Way Isolation valve • Provide and install two rupture disk and Disk Holders. • Provide new Gaskets and Bolts Reinstall Spring loaded relief disks after the rupture disks. NOT INCLUDED • Piping modifications needed to connect out of the dual relief assembly to the common header • New spring relief Valve Partial Billing of $13016.54 PO from Dupont Remaining amount of $4000.00 will be billed when valves come in |  | Custom Quote | 2014-03-22 | 2014-04-17 13:39 | 2014-03-26 15:58 | Closed | Closed | 2014-03-28 11:19
2014-03-13 13:04 | Closed | 1-9416568627 | LGGC21128 | Replace all Transducers and Temperature Sensors on CH 10 Order a backup set of sensors and transducers for spare parts. |  | Custom Quote | 2014-03-22 | 2014-03-24 13:28 | 2014-03-24 13:28 | Closed | Closed | 2014-03-15 13:04
2014-03-06 09:48 | Closed | 1-9307117648 | LOX600371 | Furnish qty-1 55 gallon drum of new York "J" oil. Furnish qty-3 5 gallon containers of new York "J" oil. Shipping included. Pricing: York "J" oil 5 gallon container $756.00 each. York "J" oil 55 gallon container $8,427.00 |  | Custom Quote |  | 2014-03-19 10:28 | 2014-03-19 10:28 | Closed | Closed | 2014-03-08 09:48
2014-02-14 11:34 | Closed | 1-8972377924 | LGGC20932 | Tube Plugging during Eddy Current Test on the Evaporator Tubes CH#6 |  | Custom Quote | 2014-02-14 | 2014-02-19 08:44 | 2014-02-19 08:44 | Closed | Closed | 2014-02-16 11:34
2014-02-12 11:17 | Closed | 1-8936306112 | LOX598048 | Eddy Current test the condenser and sub cooler tubes on Chiller #6 Provide a detailed report on the condition of the tubes The tubes must be cleaned prior to testing. Exclusions Tube cleaning Tube Plugging |  | Custom Quote |  | 2014-02-19 10:10 | 2014-02-19 10:10 | Closed | Closed | 2014-02-14 11:17
2014-02-04 14:12 | Closed | 1-8817876517 | LOX598757 | Perform Eddy Current Test on the Evaporator Tubes CH#6 Provide a detailed report of the test Tubes must be cleaned prior to testing Exclusions Tube Cleaning Tube Plugging Head Removal |  | Custom Quote | 2014-02-14 | 2014-02-18 13:12 | 2014-02-18 13:12 | Closed | Closed | 2014-02-06 14:12
2014-01-21 08:42 | Closed | 1-8552733559 | LOX597975 | * Mobilize/lock out equipment *Recover Refrigerant *Dissassemble and Inspect Compressor. Record Existing Tolerances *Reassemble Compressor with new bearings, seals, and gaskets *Realign motor to compressor *Pressure test and leak test the unit *Evacuate and recycle the refrigerant into the unit *Start, Teat and Adjust Not Included *Additional Refrigerant *Required Scaffolding |  | Custom Quote | 2014-03-25 | 2014-03-26 10:01 | 2014-03-26 10:01 | Closed | Closed | 2014-01-23 08:42
2014-01-20 10:09 | Closed | 1-8542784246 | LGGC20800 | Plugging a tube on a chiller |  | Labor & Material | 2014-01-21 | 2014-01-30 11:32 | 2014-01-30 11:32 | Closed | Closed | 2014-01-22 10:09
2014-01-10 09:11 | Closed | 1-8412597585 | Raul Cozza | *Eddy current test the condenser tubes * Provide report on the condition of the tubes * Tubes must be cleaned prior to the test Exclusions Tube cleaning Head removal Tube plugging |  | Custom Quote | 2014-01-13 | 2014-02-11 10:52 | 2014-02-11 10:51 | Closed | Closed | 2014-01-12 09:11
2014-01-08 11:53 | Cancelled | 1-8369169561 |  | Perform Eddy Current Test on condenser tubes for Chiller #7 |  | Custom Quote |  | 2014-01-10 09:13 | 2014-01-10 09:13 | Cancelled | Created In Error | 2014-01-10 11:53
2014-01-08 07:29 | Closed | 1-8363544161 | LOX597574 | INCLUDED • Disassemble and remove existing Pin Relief Valve. • Provide and install a 3 Way Isolation valve • Provide and install two rupture disk and Disk Holders. • Provide new Gaskets and Bolts Reinstall Spring loaded relief disks after the rupture disks. NOT INCLUDED • Piping modifications needed to connect out of the dual relief assembly to the common header • New spring relief Valve |  | Custom Quote |  | 2014-04-24 11:10 | 2014-04-24 11:10 | Closed | Closed | 2014-01-10 07:29
2014-01-01 08:31 | Closed | 1-8239142748 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2014-04-23 | 2014-07-31 21:57 | 2014-07-31 21:57 | Closed | Closed | 2014-01-03 08:31
2013-11-01 08:00 | Closed | 1-7368924475 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2014-01-21 | 2014-01-31 11:04 | 2014-01-31 11:04 | Closed | Closed | 2013-11-03 08:00
2013-10-04 13:34 | Closed | 1-7276250083 |  | Temp adjustment Bldg E336 |  | Labor & Material | 2013-10-05 | 2013-10-28 15:30 | 2013-10-28 15:30 | Closed | Closed | 2013-10-06 13:34
2013-10-02 12:58 | Closed | 1-7265537958 | LOX589867 | Furnish Lithium Molybdate inhibitor in qty-3 absorption chillers as needed based on analysis results. |  | Custom Quote |  | 2013-10-31 10:06 | 2013-10-31 10:06 | Closed | Closed | 2013-10-04 12:58
2013-08-20 18:56 | Closed | 1-7103037037 | LMCH11867 | Absorber #4 micro gateway is not communicating |  | Labor & Material | 2013-08-28 | 2013-09-18 13:01 | 2013-09-18 13:00 | Closed | Closed | 2013-08-22 18:56
2013-07-16 08:58 | Closed | 1-6969912043 | LOX589867 | ABSORBER CHILLER #2 DOWN |  | Labor & Material | 2013-07-16 | 2013-07-30 13:59 | 2013-07-30 13:59 | Closed | Closed | 2013-07-18 08:58
2013-07-10 08:42 | Closed | 1-6950972053 | LOX591186 | Add lithium Bromide to absorber #2 |  | Custom Quote | 2013-07-31 | 2016-04-20 08:03 | 2016-04-20 08:03 | Closed | Closed | 2013-07-12 08:42
2013-07-01 12:26 | Closed | 1-6925972819 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2013-09-06 | 2013-09-22 21:47 | 2013-09-22 21:47 | Closed | Closed | 2013-07-03 12:26
2013-06-26 11:27 | Closed | 1-6900000669 | LOX589867 | Labor to install inhibitor in Absorber Chiller |  | Labor & Material | 2013-06-26 | 2013-06-28 12:25 | 2013-06-28 12:24 | Closed | Closed | 2013-06-28 11:27
2013-06-25 11:43 | Closed | 1-6895023658 | LOX589867 | PROBLEM WITH ABSORBER CHILLER #9 |  | Labor & Material | 2013-06-25 | 2013-06-27 11:01 | 2013-06-27 11:01 | Closed | Closed | 2013-06-27 11:43
2013-06-18 10:53 | Closed | 1-6869910154 | LOX590515 | Furnish Lithium Molybdate inhibitor in qty-3 absorption chillers as needed based on analysis results. |  | Custom Quote |  | 2013-06-25 11:48 | 2013-06-25 11:48 | Closed | Closed | 2013-06-20 10:53
2013-06-05 07:25 | Closed | 1-6829119961 | LOX589867 | DE-CRYSTALIZED ABSORBER #2 |  | Labor & Material | 2013-06-05 | 2013-06-24 11:47 | 2013-06-24 11:47 | Closed | Closed | 2013-06-07 07:25
2013-04-29 08:56 | Closed | 1-6696323989 | LOX588443 | Proposal to plug chiller 9 and chiller 10 |  | Custom Quote | 2013-04-30 | 2013-05-01 14:35 | 2013-05-01 14:34 | Closed | Closed | 2013-05-01 08:56
2013-04-17 14:13 | Closed | 1-6662123802 | LOX583374 | Provide eddycurrent testing on all condenser and evaporator tubes on chillers #8, 9, and 10. Note: Head removal and tube cleaning provided by others. CH-8 m/n OTT4G2-ZBES s/n GACM117864 CH-9 m/n OTT4G2-ZBES s/n GACM127698 CH-10 m/n OTT4G2-ZBES s/n GACM127699 |  | Custom Quote | 2013-04-23 | 2013-04-30 15:14 | 2013-04-30 15:14 | Closed | Closed | 2013-04-19 14:13
2013-04-01 08:36 | Closed | 1-6608989438 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2013-05-03 | 2013-09-12 17:21 | 2013-09-12 17:21 | Closed | Closed | 2013-04-03 08:36
2013-02-28 13:06 | Closed | 1-6482766674 | LOX585576 | Rupture disk replacement Chiller 8 and two spare disks. 8 hours labor to include: Three Disks One Disk Holder |  | Custom Quote | 2013-04-11 | 2013-08-19 13:29 | 2013-08-19 13:29 | Closed | Closed | 2013-03-02 13:06
2013-02-25 09:11 | Closed | 1-6465393059 | LOX585468 | Furnish qty-1 55 gallon container of York "K" oil |  | Custom Quote |  | 2013-03-06 15:12 | 2013-03-06 15:12 | Closed | Closed | 2013-02-27 09:11
2013-01-16 08:44 | Closed | 1-6308784998 | LOX583896 | Budgetary proposal to rebuild compressor on Chiller #8. m/n OTT4G2-ZBES s/n GACM117864 Lock out / tag out all energy sources Recover and store all refrigerant using plant recovery system Disconnect compressor coupling Disconnect all compressor piping Set up rigging and lower compressor to ground Record compressor thrust and runout readings Disassemble entire compressor and evaluate all parts Furnish and install new compressor bearings and gaskets Record compressor thrust and runout readings after rebuild Rig compressor onto chiller Reconnect all piping Pressure test system with nitrogen and leak test Check and adjust motor alignment as needed Reassemble compressor coupling Evacuate system and charge with recovered refrigerant Run chiller and check operation Provide all documentation Note: Pricing per chiller. 50,066.00 |  | Custom Quote | 2013-01-31 | 2013-02-12 13:02 | 2013-02-12 13:02 | Closed | Closed | 2013-01-18 08:44
2013-01-01 10:51 | Closed | 1-6247036719 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2013-03-04 | 2013-09-12 11:36 | 2013-09-12 11:36 | Closed | Closed | 2013-01-03 10:51
2012-11-19 08:58 | Closed | 1-6073656448 | LOX581421 | MATERIAL ONLY Furnish qty-1 55 gal. drum of York "K" oil |  | Custom Quote |  | 2013-02-12 13:02 | 2013-02-12 13:01 | Closed | Closed | 2012-11-21 08:58
2012-11-01 11:42 | Closed | 1-6002646799 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2013-03-02 | 2013-03-20 09:11 | 2013-03-20 09:11 | Closed | Closed | 2012-11-03 11:42
2012-08-29 07:48 | Closed | 1-5710749030 | LDFS25135 | PARTS ORDER DuPont Experimental Station Absorber #2 m/n YPCST226-46-CXA s/n GADM248980 •Furnish and install qty-1 new absorber pump impeller. •Run unit and check operation. |  | Custom Quote |  | 2012-09-26 17:12 | 2012-09-26 17:12 | Closed | Closed | 2012-08-31 07:48
2012-08-02 10:09 | Closed | 1-5591819781 | LGGC16834 | Repair Absorber #2 Solution Pump. Furnish and install qty-1 new pump motor with repair kit. Furnish and install qty-1 new pump overload relay Furnish and install qty-1 new pump contactor. Start pump and check operation. |  | Custom Quote | 2012-08-29 | 2012-09-14 10:46 | 2012-09-14 10:46 | Closed | Closed | 2012-08-04 10:09
2012-08-01 13:43 | Closed | 1-5587255578 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2013-03-14 | 2013-03-20 09:29 | 2013-03-20 09:29 | Closed | Closed | 2012-08-03 13:43
2012-07-30 16:47 | Closed | 1-5570855801 |  | ABSORBER PUMP DOWN |  | Labor & Material | 2012-07-30 | 2012-08-16 12:18 | 2012-08-16 12:18 | Closed | Closed | 2012-08-01 16:47
2012-07-19 07:36 | Closed | 1-5515764727 |  | Preventive Maintenance | Non billable SR | Scheduled Service | 2012-08-02 | 2012-08-29 14:27 | 2012-08-29 14:27 | Closed | Closed | 2012-07-21 07:36
2012-06-12 10:51 | Cancelled | 1-5326246850 |  | Take service call on Absorber #2 down. Have operators switch over to chiller start chiller #2. Start chiller and begin to check operation. Building had fire alarm and had to be evacuated. Upon return check out and log chiller #2 and check operation. Also check operation of absorbers #1,and #3. |  | Custom Quote |  | 2012-06-25 10:22 | 2012-06-25 10:22 | Cancelled | Created In Error | 2012-06-14 10:51
2012-06-12 10:08 | Closed | 1-5326338169 | LGGC16318 | Use PO LGGC16318 DuPont Experimental Station Wilmington, DE •Furnish and install Lithium Molybdate inhibitor in qty-4 absorption chillers as needed based on analysis results. |  | Custom Quote | 2012-07-02 | 2012-09-14 11:09 | 2012-09-14 11:09 | Closed | Closed | 2012-06-14 10:08
2012-06-05 08:33 | Closed | 1-5291903176 | LOX574005 | Use PO # LOX574005 •Furnish qty-2 new purge transducers p/n 025-29907-002. |  | Custom Quote |  | 2012-06-28 14:34 | 2012-06-28 14:34 | Closed | Closed | 2012-06-07 08:33
2012-05-29 09:25 | Cancelled | 1-5249959211 |  | Service call to address problem with absorber #2 Quote needed from job before billing ACTIVITY MOVED TO SR#1-5326246850. |  | Labor & Material |  | 2012-06-12 10:49 | 2012-06-12 10:49 | Cancelled | Created In Error | 2012-05-31 09:25
2012-05-25 08:20 | Closed | 1-5238056088 | LGGC16094 | DuPont Experimental Station Absorber #3 m/n YPCST226-46-CXA s/n GADM233620 •Respond to service call on unit shutting down on “High first stage generator temperature”. •Run unit through de-crystallization procedure. •Apply external heat to liquefy stubborn areas. •Run unit and check operation. |  | Custom Quote | 2012-05-07 | 2012-05-30 12:39 | 2012-05-30 12:39 | Closed | Closed | 2012-05-27 08:20
2012-05-07 12:26 | Cancelled | 1-5146711973 |  | DE-CRYSTALIZING ABSORBER #3 (Activity needs to be moved to SR#1-5238056088) then billed as quoted job. |  | Labor & Material |  | 2012-05-25 09:38 | 2012-05-25 09:38 | Cancelled | Created In Error | 2012-05-09 12:26
2012-04-03 08:32 | Closed | 1-4972943318 | LGGC15615 | USE PO# LGGC15615 Chiller #10 Job Scope: Furnish and install qty-1 Norris Valve seal kit. •Lock out / Tag out all energy sources. •Furnish and install qty-1 valve O-ring kit for free cooling valve. •Pressurize and leak check new valve. •Clean up chiller. •Check operation. •Note: Refrigerant recovery and recharge performed by others. |  | Custom Quote | 2012-04-24 | 2013-06-24 14:23 | 2013-06-24 14:22 | Closed | Closed | 2012-04-05 08:32
2012-04-03 08:27 | Closed | 1-4972942980 | LGGC15614 | Use PO#LGGC15614 Chiller #9 Job Scope: Furnish and install qty-1 Norris Valve seal kit. •Lock out / Tag out all energy sources. •Furnish and install qty-1 valve O-ring kit for free cooling valve. •Pressurize and leak check new valve. •Clean up chiller. •Check operation. •Note: Refrigerant recovery and recharge performed by others. |  | Custom Quote | 2012-05-05 | 2012-09-14 11:02 | 2012-09-14 11:02 | Closed | Closed | 2012-04-05 08:27
2012-03-31 14:34 | Closed | 1-4963268475 |  | Preventive Maintenance |  | Scheduled Service | 2012-05-29 | 2013-03-20 08:53 | 2013-03-20 08:53 | Closed | Closed | 2012-04-02 14:34
2012-03-12 09:03 | Closed | 1-4856238148 | LGGC15395 | Use PO#LGGC15395 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 Norris Valve seal kit. •Lock out / Tag out all energy sources. •Furnish and install qty-1 valve O-ring kit. •Pressurize and leak check new valve. •Check operation. |  | Custom Quote | 2012-04-04 | 2012-09-14 10:56 | 2012-09-14 10:56 | Closed | Closed | 2012-03-14 09:03
2012-03-09 16:30 | Closed | 1-4849659201 | LGGC15435 | BLDG 336 CHILLER IN ALARM |  | Labor & Material | 2012-03-10 | 2012-03-15 09:14 | 2012-03-15 09:14 | Closed | Closed | 2012-03-11 16:30
2012-02-29 13:13 | Closed | 1-4794930239 | LGGC14985 | THIS IS 2 OF 2 ( PARTIAL BALANCE ) Original SR 1-4712912261 has been billed for $12,000.00 USE PO# LGGC14985 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. •Lock out / Tag out all energy sources. •Recover and weigh entire refrigerant charge using plant recovery system. •Disassemble compressor coupling. •Remove and replace compressor shaft seal. •Leak test entire chiller with nitrogen. •Evacuate chiller and perform vacuum hold test. •Check coupling alignment using laser alignment tool. •Reassemble compressor coupling. •Charge chiller with recovered refrigerant. •Furnish and install 20 gallons of new compressor oil. •Run chiller and check operation. |  | Custom Quote | 2012-03-21 | 2012-03-27 14:31 | 2012-03-27 14:31 | Closed | Closed | 2012-03-02 13:13
2012-02-29 12:16 | Cancelled | 1-4793406009 | LGGC14985 | PART TWO OF JOB. WILL NEED TO TURN INTO QUOTE USE PO# LGGC14985 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. •Lock out / Tag out all energy sources. •Recover and weigh entire refrigerant charge using plant recovery system. •Disassemble compressor coupling. •Remove and replace compressor shaft seal. •Leak test entire chiller with nitrogen. •Evacuate chiller and perform vacuum hold test. •Check coupling alignment using laser alignment tool. •Reassemble compressor coupling. •Charge chiller with recovered refrigerant. •Furnish and install 20 gallons of new compressor oil. •Run chiller and check operation. |  | Custom Quote |  | 2012-02-29 13:37 | 2012-02-29 13:37 | Cancelled | Created In Error | 2012-03-02 12:16
2012-02-14 12:01 | Closed | 1-4712912261 | LGGC14985 | USE PO# LGGC14985 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. Lock out / Tag out all energy sources. Recover and weigh entire refrigerant charge using plant recovery system. Disassemble compressor coupling. Remove and replace compressor shaft seal. Leak test entire chiller with nitrogen. Evacuate chiller and perform vacuum hold test. Check coupling alignment using laser alignment tool. Reassemble compressor coupling. Charge chiller with recovered refrigerant. Furnish and install 20 gallons of new compressor oil. Run chiller and check operation. |  | Custom Quote | 2012-02-25 | 2017-02-10 18:46 | 2012-09-14 10:53 | Closed | Closed | 2012-02-16 12:01
2012-02-07 14:29 | Cancelled | 1-4673843608 |  | DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. •Lock out / Tag out all energy sources. •Recover and weigh entire refrigerant charge using plant recovery system. •Disassemble compressor coupling. •Remove and replace compressor shaft seal. •Leak test entire chiller with nitrogen. •Evacuate chiller and perform vacuum hold test. •Check coupling alignment using laser alignment tool. •Reassemble compressor coupling. •Charge chiller with recovered refrigerant. •Run chiller and check operation. |  | Custom Quote |  | 2012-02-14 12:08 | 2012-02-14 12:08 | Cancelled | Created In Error | 2012-02-09 14:29
2012-01-22 15:18 | Closed | 1-4574444162 | LGGC14883 | DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 Job Scope: •Premium time for work performed by Mike Ianovale and Joe Fisher on Saturday 1-7-12. |  | Custom Quote | 2012-01-07 | 2012-01-23 13:35 | 2012-01-23 13:35 | Closed | Closed | 2012-01-24 15:18
2012-01-20 15:02 | Cancelled | 1-4566677889 |  | PREMIUM TIME COVERAGE NEEDED FOR EQUIPMENT REPAIR weekend of 1/7/2012. premium time to start and test chiller#7 for the hot alignment check |  | Custom Quote |  | 2012-01-22 15:35 | 2012-01-22 15:35 | Cancelled | Created In Error | 2012-01-22 15:02
2012-01-17 11:13 | Closed | 1-4544978844 | LGGC14775 | use po# LGGC14775 DuPont Experimental Station Chiller #7. •Furnish and install qty-1 new additional bursting disk relief indicators for refrigerant relief valves. •Isolate, lock out and tag out valves as required. •Disassemble assembly and clean all gasket surfaces. •Furnish and install new bursting disk and gaskets. •Leak test assembly. |  | Custom Quote | 2012-04-30 | 2012-04-30 16:03 | 2012-04-30 16:03 | Closed | Closed | 2012-01-19 11:13
2012-01-09 09:04 | Cancelled | 1-4491902342 |  | PREMIUM TIME COVERAGE NEEDED FOR EQUIPMENT REPAIR ** PAUL NEEDS TO CONVERT TO QUOTED PRICE ** Cancelled. |  | Labor & Material |  | 2012-01-20 15:07 | 2012-01-20 15:06 | Cancelled | Created In Error | 2012-01-11 09:04
2012-01-01 07:45 | Closed | 1-4458302276 |  | Preventive Maintenance |  | Scheduled Service | 2012-05-09 | 2013-03-20 08:36 | 2013-03-20 08:36 | Closed | Closed | 2012-01-03 07:45
2011-12-05 10:15 | Closed | 1-4311150501 | LGGC14480 | USE PO# DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 •Furnish qty-1 new seal end compressor bearing. •Furnish qty-1 new Pump end compressor bearing. •Furnish qty-1 new reverse thrust bearing. |  | Custom Quote | 2011-12-14 | 2011-12-14 09:08 | 2011-12-14 09:08 | Closed | Closed | 2011-12-07 10:15
2011-11-29 15:15 | Closed | 1-4276984327 | LGGC14336 | USE PO# LGGC14336 DuPont Experimental Station Chiller #7. •Furnish and install qty-5 new bursting disk relief indicators for refrigerant relief valves. oQty-2 disks on Chiller #7 Evaporator oQty-2 disks on refrigerant recovery receiver. oQty-1 disk on refrigerant recovery unit. •Isolate, lock out and tag out valves as required. •Disassemble assemblies and clean all gasket surfaces. •Furnish and install new bursting disks and gaskets. •Leak test each assembly. |  | Custom Quote | 2012-02-04 | 2012-02-06 13:21 | 2012-02-06 13:21 | Closed | Closed | 2011-12-01 15:15
2011-11-29 13:31 | Closed | 1-4276011500 | LGGC14336 | USE PO#LGGC14336 DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 Job Scope: Perform compressor bearing inspection and coupling alignment on qty-1 York OM chiller. •Lock out / Tag out chiller. •Transfer refrigerant charge to storage vessel using plant transfer system. •Disassemble compressor coupling. •Check and record compressor shaft runout and thrust readings. •Drain oil from compressor. •Dissemble compressor oil sump cover and oil pump. •Remove and inspect front compressor bearing. •Disassemble compressor shaft seal. •Remove and inspect rear compressor bearing. •Reassemble both compressor bearing assemblies with new gaskets. •Furnish and install new compressor shaft seal. •Recheck compressor runout and thrust readings. •Install new compressor oil and filters. (Supplied by customer) •Pressurize compressor with nitrogen and leak test. •Disassemble motor to gearbox coupling. •Check and record alignment of both couplings using laser tool and dial indicators. •Adjust alignments if needed to bring within factory specs. •Perform coupling maintenance. •Reassemble both couplings. •Evacuate system and perform vacuum hold test. •Recharge chiller with recovered refrigerant. •Check chiller operation. •Provide all documentation. |  | Custom Quote | 2011-12-23 | 2013-09-29 18:34 | 2013-09-29 18:34 | Closed | Closed | 2011-12-01 13:31
2011-11-29 13:24 | Closed | 1-4276011474 | LGGC14377 | USE PO# LGGC14377 DuPont Experimental Station Absorbers. #1 m/n YPCST22G46CXA s/n GLCM157836. #2 m/n YPCST22G46CXA s/n GBDM248980. #3 m/n YPCST22G46CXA s/n GADM233620. #4 m/n YPCST22G46CXA s/n GNCM9423001. Job Scope: Furnish and install new non-fragmenting type bursting disks and disk holders on each chiller. (Qty-2 per chiller. Total of qty-8). •Lock out / Tag out chiller. •Remove old carbon type disks and gaskets. •Re-fabricate piping as needed to accept new disk holders. •Furnish and install new disks and disk holders. •Pressurize and leak check around new bursting disks. •Provide all documentation. |  | Custom Quote | 2012-02-11 | 2012-04-02 14:59 | 2012-04-02 14:58 | Closed | Closed | 2011-12-01 13:24
2011-11-10 07:33 | Closed | 1-4191187406 |  | Preventive Maintenance |  | Scheduled Service | 2012-01-10 | 2013-03-20 08:29 | 2013-03-20 08:29 | Closed | Closed | 2011-11-12 07:33
2011-11-03 15:35 | Cancelled | 1-4160612327 | LGGC14144 | USE PO# LGGC14144 DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 Job Scope: Perform motor, gearbox, and compressor coupling alignment. •Lock out / Tag out chiller •Disassemble motor to gearbox and gearbox to compressor couplings. •Check and record alignment of both couplings using laser tool and dial indicators. •Adjust alignments if needed to bring within factory specs. •Perform coupling maintenance. •Reassemble both couplings. •Check chiller operation. •Provide all documentation. |  | Custom Quote |  | 2012-04-27 10:21 | 2012-04-27 10:21 | Cancelled | Customer Cancelled | 2011-11-05 15:35
2011-11-03 13:19 | Closed | 1-4160013757 | LGGC14145 | USE PO# LGGC14145 DuPont Experimental Station Absorber #2 m/n YPCST22G46CXA s/n GBDM248980 Job Scope: Troubleshoot low refrigerant temperature alarm. •Lock out / Tag out chiller •Check refrigerant flow to spray headers. •Change refrigerant pump. (Pump supplied by customer) •Check chiller operation. •Provide all documentation. |  | Custom Quote | 2011-11-01 | 2011-11-10 11:28 | 2011-11-10 11:28 | Closed | Closed | 2011-11-05 13:19
2011-10-31 12:43 | Closed | 1-4138658401 |  | Preventive Maintenance |  | PSA Repair | 2012-05-10 | 2013-03-20 08:13 | 2013-03-20 08:13 | Closed | Closed | 2011-11-02 12:43
2011-09-22 11:16 | Closed | 1-3896106608 | LOX559651 | Material Order for (1) "55 Gallon Drum of K-Oil (011 00534 000) and (1) "5 Gallon drum of K-Oil (011 00533 000). |  | Material Only Quote |  | 2011-09-29 16:21 | 2011-09-29 16:21 | Closed | Closed | 2011-09-24 11:16
2011-09-13 09:44 | Closed | 1-3832679073 | LGGC12820 | CHILLER #3 DOWN |  | Labor & Material | 2011-09-13 | 2011-09-20 16:39 | 2011-09-20 16:39 | Closed | Closed | 2011-09-15 09:44
2011-08-10 09:39 | Closed | 1-3614184300 | LGGC12820 | POWER FAILURE - CHILLER DOWN |  | Labor & Material | 2011-08-10 | 2011-08-12 13:42 | 2011-08-12 13:42 | Closed | Closed | 2011-08-12 09:39
2011-07-13 08:51 | Closed | 1-3395663956 | LMCH10247 | Use PO# LMCH10247 DuPont Experimental Station Absorption Chillers #3 and #4 Absorber #3 m/n YPCST22G46CX s/n GADM233620 Absorber #4 m/n YPCST22G46CX s/n GNCM9423001 •Furnish and install Adva-Guard 591 chemical inhibitor for qty-2 York Absorption Chillers based on solution analysis results.. •Chiller #3…… 2.7 lbs. •Chiller #4…….2.82 lbs. |  | Custom Quote | 2011-07-28 | 2011-09-09 09:00 | 2011-07-29 15:11 | Closed | Closed | 2011-07-15 08:51
2011-07-06 14:37 | Closed | 1-3350806150 | LMCH10237 | TROUBLESHOOT AND REPAIR THE #10 CHILLER AT E315 |  | Labor & Material | 2011-07-06 | 2011-07-14 14:33 | 2011-07-14 14:33 | Closed | Closed | 2011-07-08 14:37
2011-07-01 07:51 | Closed | 1-3314236480 |  | Preventive Maintenance |  | Scheduled Service | 2011-11-04 | 2012-09-07 14:18 | 2012-09-07 14:18 | Closed | Closed | 2011-07-03 07:51
2011-06-02 10:40 | Closed | 1-3073406829 |  | Preventive Maintenance |  | Scheduled Service | 2011-07-22 | 2013-03-19 15:19 | 2013-03-19 15:19 | Closed | Closed | 2011-06-04 10:40
2011-05-12 11:17 | Closed | 1-2913970345 |  | ABSORBER PM'S |  | Scheduled Maintenance | 2011-05-12 | 2011-10-24 15:03 | 2011-10-24 15:03 | Closed | Closed | 2011-05-14 11:17
2011-04-14 12:17 | Closed | 1-2720351788 | LGGC10244 | Dupont Experimental Station Building 336. York YCAS190 Chiller. •Furnish and install qty-1 new condenser fan motor, fan blade, and blade mounting hardware. (Fan #7). •Furnish and install qty-1 new suction temperature sensor. •Furnish and install qty-1 new oil pressure transducer. •Start chiller and check operation. •Note: All work to be performed on a Saturday. NOT DONE |  | Custom Quote | 2011-04-30 | 2011-05-31 16:10 | 2011-05-31 16:10 | Closed | Closed | 2011-04-16 12:17
2011-03-31 09:39 | Closed | 1-2635588274 |  | Preventive Maintenance |  | Scheduled Service | 2011-06-01 | 2011-10-24 15:02 | 2011-10-24 15:02 | Closed | Closed | 2011-04-02 09:39
2011-03-30 11:18 | Closed | 1-2627851260 |  | PURGE PUMP MAINT. |  | Scheduled Maintenance |  | 2011-10-24 15:02 | 2011-10-24 15:02 | Closed | Closed | 2011-04-01 11:18
2011-03-16 16:36 | Closed | 1-2548420121 | LGGC9754 | E336 CHILLER SERVICE CALL..... (waiting on parts to hit job) |  | Labor & Material | 2011-03-19 | 2011-03-28 13:44 | 2011-03-28 13:44 | Closed | Closed | 2011-03-18 16:36
2011-02-16 15:56 | Closed | 1-2382254821 | LGGC8974 | Use PO # LGGC8974 DuPont Experimental Station Chiller #8. m/n OTT4G2-2BES s/n GACM117864 Furnish and install qty-1 new oil pump shaft seal kit on chiller #8. Remove and weigh refrigerant charge from chiller using plant recovery / transfer system. Disassemble oil pump and install new pump shaft seal kit. Pressurize chiller with nitrogen and leak test. Evacuate and recharge chiller with recovered refrigerant. Check oil pump operation. |  | Custom Quote | 2011-02-25 | 2011-02-28 12:28 | 2011-02-28 12:28 | Closed | Closed | 2011-02-18 15:56
2011-02-04 14:57 | Closed | 1-2322219561 | LGGC8619 | DuPont Experimental Station York Chiller #7. USE PO# LGGC8619 Furnish and install qty-1 new Monitech LCD display monitor on chiller control panel. Note: The Monitech display is an aftermarket display which replaces the tube only and utilizes the existing panel interface. ( No programming required). The original display is no longer available. |  | Custom Quote | 2011-02-22 | 2011-02-28 15:06 | 2011-02-28 15:06 | Closed | Closed | 2011-02-06 14:57
2011-01-18 15:22 | Closed | 1-2224249835 | LOX548915 | MATERIAL ORDER FOR (6) OIL FILTERS FOR YORK CHILLERS. QUOTED AMOUNT $219.90. |  | Material Only Quote |  | 2011-03-26 11:24 | 2011-03-26 11:24 | Closed | Closed | 2011-01-20 15:22
2011-01-01 11:00 | Closed | 1-2145850208 |  | Preventive Maintenance |  | Scheduled Service | 2011-05-13 | 2011-10-24 15:00 | 2011-10-24 15:00 | Closed | Closed | 2011-01-03 11:00
2010-12-27 08:06 | Closed | 1-2110929898 | CAROL BAFFONE | •Furnish and install qty-10 new gaskets on bursting disk relief indicators for refrigerant relief valves. •Isolate, lock out and tag out valves as required. •Disassemble assemblies and clean all gasket surfaces. •Furnish and install new gaskets. •Leak test each assembly. |  | Custom Quote | 2010-12-28 | 2010-12-30 10:28 | 2010-12-30 10:28 | Closed | Closed | 2010-12-29 08:06
2010-12-18 09:12 | Closed | 1-2083406911 |  | YCAS190 chiller was experiencing a low temperature alarm. |  | Labor & Material | 2010-12-18 | 2010-12-21 13:00 | 2010-12-21 13:00 | Closed | Closed | 2010-12-20 09:12
2010-12-08 09:56 | Closed | 1-2031869374 | LGGC7651 | Provide Eddy current testing on all condenser and evaporator tubes on Chiller #7. Furnish detailed report of tube condition in hard copy and PDF format. Note: Condenser and evaporator heads must be removed and all tubes must be brush cleaned before testing can begin. (Performed by others). |  | Custom Quote | 2010-12-20 | 2011-01-12 12:05 | 2011-01-12 12:05 | Closed | Closed | 2010-12-10 09:56
2010-12-07 14:41 | Cancelled | 1-2027396439 |  | EDDY CURRENT TESTING - ACTIVITY TO BE MOVED AFTER COMPLETION OF QUOTE. |  | Labor & Material |  | 2010-12-08 10:02 | 2010-12-08 10:02 | Cancelled | Created In Error | 2010-12-09 14:41
2010-11-15 21:59 | Closed | 1-1907409794 |  | ABSORBER SHUTDOWN |  | Scheduled Maintenance | 2010-11-26 | 2011-10-18 16:44 | 2011-03-22 14:55 | Closed | Closed | 2010-11-17 21:59
2010-10-31 12:26 | Closed | 1-1828518509 |  | Preventive Maintenance |  | Scheduled Service | 2010-11-15 | 2011-10-24 14:59 | 2011-10-24 14:59 | Closed | Closed | 2010-11-02 12:26
2010-10-05 10:35 | Closed | 1-1693076316 | LMCH10247 | MATERIAL QUOTE FOR INHIBITOR. |  | Material Only Quote |  | 2012-05-18 10:48 | 2012-05-18 10:48 | Closed | Closed | 2010-10-07 10:35
2010-09-23 15:50 | Closed | 1-1617871854 | LDFS25135 | Furnish and install qty-1 new keypad for Absorption chiller #1. |  | Custom Quote | 2010-09-27 | 2010-09-27 16:43 | 2010-09-27 16:43 | Closed | Closed | 2010-09-25 15:50
2010-08-14 10:32 | Closed | 1-1384543671 |  | REPAIRS TO RTU BLDING 336 (WEEKEND ACCESS) |  | Labor & Material | 2010-08-14 | 2010-08-31 11:45 | 2010-08-31 11:45 | Closed | Closed | 2010-08-16 10:32
2010-08-09 20:17 | Closed | 1-1357550573 |  | Preventive Maintenance |  | Scheduled Service | 2010-09-21 | 2011-10-24 14:57 | 2011-10-24 14:57 | Closed | Closed | 2010-08-11 20:17
2010-08-09 16:44 | Closed | 1-1356202728 |  | OPERATIONAL SSV'S |  | Scheduled Maintenance | 2010-09-30 | 2011-10-24 14:57 | 2011-10-24 14:57 | Closed | Closed | 2010-08-11 16:44
2010-08-04 14:26 | Closed | 1-1329193316 | LGGC4301 | ABSORBER #2 DOWN ON LOW REFRIGERANT |  | Labor & Material | 2010-08-05 | 2010-08-06 15:11 | 2010-08-06 15:10 | Closed | Closed | 2010-08-06 14:26
2010-07-30 14:50 | Closed | 1-1297135051 | LGGC4301 | ABS 2 Leak Repairs |  | Labor & Material | 2010-08-03 | 2010-08-16 12:28 | 2010-08-04 08:54 | Closed | Closed | 2010-08-01 14:50
2010-07-23 10:23 | Closed | 1-1249898436 |  | REPAIRS TO RTU IN BLDG 336. FIRST CALL - SERVICE CALL ON SATURDAY. |  | Labor & Material | 2010-07-24 | 2010-08-31 11:44 | 2010-08-31 11:44 | Closed | Closed | 2010-07-25 10:23
2010-07-12 11:19 | Closed | 1-1189019721 | LGGC4301 | PARTIAL BILLING - PURGE UNIT ON #2 CHILLER MALFUNCTIONING. |  | Labor & Material | 2010-07-30 | 2010-07-30 15:34 | 2010-07-30 15:33 | Closed | Closed | 2010-07-14 11:19
2010-06-14 08:55 | Closed | 1-1021703411 | LGGC4301 | CHILLER #3 OFFLINE |  | PSA Repair | 2010-07-06 | 2011-10-18 16:43 | 2010-07-07 11:03 | Closed | Closed | 2010-06-16 08:55
2010-06-09 09:15 | Closed | 1-996861621 |  | Perform seasonal maintenance on qty-1 YCAS0190 air-cooled chiller. Clean all condenser coils with pressure washer. Change compressor oil filter. Leak check entire chiller.Perform oil and refrigerant analysis. Check all condenser fan motors and blades. Check all chiller safeties and controls. Megger test compressor motor. Check compressor starter and tighten all connections. Start chiller and check operation. Note: All work to be performed on overtime. |  | Custom Quote | 2010-06-12 | 2010-06-15 15:41 | 2010-06-15 15:41 | Closed | Closed | 2010-06-11 09:15
2010-06-01 09:39 | Closed | 1-951443420 |  | PM ON ABSORBERS |  | Scheduled Maintenance | 2011-06-09 | 2011-10-24 15:05 | 2011-10-24 15:05 | Closed | Closed | 2010-06-03 09:39
2010-05-26 08:46 | Closed | 1-904072214 | LGGC24TS | FINISH AND INSTALL (1) NEW LOW REFRIGERANT TEMP SWITCH. |  | Custom Quote | 2010-05-27 | 2010-06-29 13:08 | 2010-06-29 13:08 | Closed | Closed | 2010-05-28 08:46
2010-05-13 08:17 | Closed | 1-832516755 |  | BASIC SEASONAL MAINT. |  | Scheduled Maintenance | 2010-05-28 | 2011-10-18 16:43 | 2010-05-29 11:15 | Closed | Closed | 2010-05-15 08:17
2010-04-14 07:57 | Closed | 1-672193722 |  | Preventive Maintenance |  | Scheduled Service | 2010-08-09 | 2011-10-24 15:04 | 2011-10-24 15:04 | Closed | Closed | 2010-04-16 07:57
2010-04-01 18:23 | Closed | SR:92607131 |  | Vendor PO Data Conversion USE ONLY - DO NOT USE SR FOR CREATING NEW CONTRACT ACTIVITIES |  | PSA Repair | 2010-04-08 | 2010-04-01 18:23 |  | Closed | Closed