CHILLER #7 OIL SUMP SIGHTGLASS REPLACEMENT
DUPONT PO#: 6501821002
JCI QUOTE#: 1-R0IFJSX
SR: 1-58806996905

- Due to Hairline Fractures in the Bottom Compressor Oil Sump Sight Glass, the Oil Charge was temporarily transferred into a clean drum, seal & pressurized with dry Nitrogen (to prevent moisture saturation).

- Bottom sight-glass was removed, oil sump surfaces cleaned, & New Sight-glass install with New O-ring Seal.

    Sight-glass: 026-13123-000
    O-ring: 028-07998-000

- New Sight-glass was verified Leak-Free when Entire Chiller was Leak Tested at 100psig of Nitrogen on 12/22/17.
- Oil will be re-installed after other maintenance items are completed.