¬

 Easylink 2.4 P76
 Registered to Kevin Fraze, Johnson Controls

 Filename:   	7 LS CP 1          
 Date:       	05.May.2017
 Time:       	14:22
 Program:    	Horizontal          
 Unit:       	thou (thou/in)
 Serial:    	43278 / 43331 / 43305
 Temp:       	 

 S-M:       	10.0
 S-Center:   	5.0
 S-Foot1:    	26.0
 S-Foot2:    	76.0
 
 V/H	 Offset	 Angle	 Foot1	 Foot2
 ------------------------------------------------------------
 H 	 1.05	 0.10	 3.50	 9.30
 V 	 6.65	 0.00	 6.65	 6.60
 ------------------------------------------------------------
 
 Comp 	 Offset	 Angle
 ------------------------------------------------------------
 H 	 0.00	 0.00
 V 	 0.00	 0.00
 ------------------------------------------------------------

 ¬

 Easylink 2.4 P76
 Registered to Kevin Fraze, Johnson Controls

 Filename:   	7 LS CP 1          
 Date:       	05.May.2017
 Time:       	14:25
 Program:    	Horizontal          
 Unit:       	thou (thou/in)
 Serial:    	43278 / 43331 / 43305
 Temp:       	 

 S-M:       	10.0
 S-Center:   	5.0
 S-Foot1:    	26.0
 S-Foot2:    	76.0
 
 V/H	 Offset	 Angle	 Foot1	 Foot2
 ------------------------------------------------------------
 H 	 1.00	 0.10	 3.50	 9.45
 V 	 6.65	 0.00	 6.65	 6.60
 ------------------------------------------------------------
 
 Comp 	 Offset	 Angle
 ------------------------------------------------------------
 H 	 0.00	 0.00
 V 	 0.00	 0.00
 ------------------------------------------------------------

 

 
 ¬

 Easylink 2.4 P76
 Registered to Kevin Fraze, Johnson Controls

 Filename:   	7LSCP2             
 Date:       	05.May.2017
 Time:       	14:34
 Program:    	Horizontal          
 Unit:       	thou (thou/in)
 Serial:    	43278 / 43331 / 43305
 Temp:       	 

 S-M:       	10.0
 S-Center:   	5.0
 S-Foot1:    	26.0
 S-Foot2:    	76.0
 
 V/H	 Offset	 Angle	 Foot1	 Foot2
 ------------------------------------------------------------
 H 	-0.95	-0.05	-1.80	-3.85
 V 	 6.45	 0.05	 7.75	 10.80
 ------------------------------------------------------------
 
 Comp 	 Offset	 Angle
 ------------------------------------------------------------
 H 	 0.00	 0.00
 V 	 0.00	 0.00
 ------------------------------------------------------------

 

 
 
 ¬

 Easylink 2.4 P76
 Registered to Kevin Fraze, Johnson Controls

 Filename:   	7LSCP3             
 Date:       	05.May.2017
 Time:       	14:37
 Program:    	Horizontal          
 Unit:       	thou (thou/in)
 Serial:    	43278 / 43331 / 43305
 Temp:       	 

 S-M:       	10.0
 S-Center:   	5.0
 S-Foot1:    	26.0
 S-Foot2:    	76.0
 
 V/H	 Offset	 Angle	 Foot1	 Foot2
 ------------------------------------------------------------
 H 	-1.05	-0.05	-2.35	-5.45
 V 	 6.35	 0.00	 6.20	 5.80
 ------------------------------------------------------------
 
 Comp 	 Offset	 Angle
 ------------------------------------------------------------
 H 	 0.00	 0.00
 V 	 0.00	 0.00
 ------------------------------------------------------------

 

 
 ¬

 Easylink 2.4 P76
 Registered to Kevin Fraze, Johnson Controls

 Filename:   	7LSCP W_SF         
 Date:       	05.May.2017
 Time:       	15:35
 Program:    	Horizontal          
 Unit:       	thou (thou/in)
 Serial:    	43278 / 43331 / 43305
 Temp:       	 

 S-M:       	10.0
 S-Center:   	5.0
 S-Foot1:    	26.0
 S-Foot2:    	76.0
 
 V/H	 Offset	 Angle	 Foot1	 Foot2
 ------------------------------------------------------------
 H 	-1.20	-0.10	-3.25	-8.10
 V 	 6.50	 0.00	 6.85	 7.80
 ------------------------------------------------------------
 
 Comp 	 Offset	 Angle
 ------------------------------------------------------------
 H 	 0.00	 0.00
 V 	 0.00	 0.00
 ------------------------------------------------------------

 

¬

 Easylink 2.4 P76
 Registered to Kevin Fraze, Johnson Controls

 Filename:   	7HSUC 1            
 Date:       	09.May.2017
 Time:       	15:16
 Program:    	Horizontal          
 Unit:       	thou (thou/in)
 Serial:    	43278 / 43331 / 43305
 Temp:       	 

 S-M:       	14.0
 S-Center:   	11.9
 S-Foot1:    	21.7
 S-Foot2:    	40.7
 
 V/H	 Offset	 Angle	 Foot1	 Foot2
 ------------------------------------------------------------
 H 	 0.45	 0.00	 0.40	 0.30
 V 	-7.90	-0.20	-9.80	-13.40
 ------------------------------------------------------------
 
 Comp 	 Offset	 Angle
 ------------------------------------------------------------
 H 	 0.00	 0.00
 V 	 0.00	 0.00
 ------------------------------------------------------------

 
 
¬

 
 Easylink 2.4 P76
 Registered to Kevin Fraze, Johnson Controls

 Filename:   	7HSUC 2            
 Date:       	09.May.2017
 Time:       	15:21
 Program:    	Horizontal          
 Unit:       	thou (thou/in)
 Serial:    	43278 / 43331 / 43305
 Temp:       	 

 S-M:       	14.0
 S-Center:   	11.9
 S-Foot1:    	21.7
 S-Foot2:    	40.7
 
 V/H	 Offset	 Angle	 Foot1	 Foot2
 ------------------------------------------------------------
 H 	 1.05	 0.00	 1.25	 1.65
 V 	-7.40	-0.15	-8.70	-11.25
 ------------------------------------------------------------
 
 Comp 	 Offset	 Angle
 ------------------------------------------------------------
 H 	 0.00	 0.00
 V 	 0.00	 0.00
 ------------------------------------------------------------