- Completed Vapor Recovery of Chiller #7
- Isolated and Tagged Out #7's Refrigerant Recovery Valves.
- Transferred the Refrigerant left in the Common Recovery Liquid Line into the Central Recovery Tank to Weigh Total Charge Recovered from Chiller #7.

  NET LIQUID= 7,050 LBS
  NET VAPOR= 1,280 LBS
  NET from LIQUID LINE= 310 LBS
  TOTAL R-134A RECOVERED= 8,640 LBS
  CHILLER DESIGN CHARGE= 8,970 LBS
  CHARGE DEFICIT= 330 LBS (3.68% LOW)

- Broke #7's Vacuum with Site Nitrogen and left 5psig Static Nitrogen Charge on Chiller until Old Relief System is Ready for Removal.
- Will continue with project once Relief Header Installation is completed to Chiller Connections.