#7 SEAL OIL CALCULATION: 
02/12/2016:
RUN TOTAL= 3326Days 1Hr (79,825hrs) 
SEAL OIL TANK= EMPTY

02/09/2017:
RUN TOTAL= 3522Days 3Hrs 18Min (84,531hrs) 
COMP OIL LEVEL= 1/4" Sight Glass
Added 5 Gallons K Oil
COMP OIL LEVEL= Just Above BSG

02/10/2017
RUN TOTAL= 3523Days 8Hrs 31Min (84,560.5hrs) 
Seal Oil Removed= 8.5Gallons
6.794ml/hr Leak Rate (1 Year Average)