## Sheet1
DUPONT EXPERIMENTAL STATION PO 6501690015 RUNNING TALLY
DATE | SR | DESCRIPTION | INVOICE # | INVOICE AMOUNT | SERVICE REPORT SENT
2017-01-10 | 1-45487366293 | Scheduling/consultive: Ruptured Disc replacements on qty 4 absorber chillers | 1-45908261249 | 293.44
1/18-19/2017 | 1-45734478692 | Consultive service of 1/18. CHILLER #9 RUPTURE DISK INSPECTION Emergency work of 1/19: CHILLER #9 RUPTURE DISK INSPECTION | 1-45908689046 | 880.32
2017-01-26 | 1-45677647587 | CHILLER #8 LOW OIL LEVEL Add appropriate amount of YORK "J" Oil (Customer Supplied) to Chiller #8 to bring back to Normal Operating Level. Measure Seal Oil Leakage and Calculate Leak rates on #8,9,&10 to determine Condition of Shaft Seals. Make necessary Adjustments on Chiller #8's Vane Arm Assembly. Change and Tighten Fasteners. Apply Sealant to Actuator Motor Shaft. QUOTE 1-K2OOT6G | 1-45908380528 | 641.7
2017-02-10 | 1-46661659154 | • Temporarily Transferred Out Remaining Refrigerant From York Central Recovery Tank and Into CHILLER #10 (720lbs) • Pumped Down Tank to 2psig (Scale Reading= 370lbs) • Reset Tank Scale To Zero Pounds • Transferred Back Into Tank 720lbs from CHILLER #10 • Noted Reset and Scale Readings on Recovery System Spreadsheet
TOTAL |  |  |  | 1815.46