## A
Johnson Controls Alignment Report
JOB: | DUPONT EXERIMENTAL STATION |  | Laser Alignment
EQUIPMENT # | CHILLER #10 |  | Dial Indicator | ✓
LOCATION: | E315 POWERHOUSE
PARALLEL ALIGNMENT
| READINGS |  | REFERENCE DATA
12:00 | 0 | REQUIRED HORIZONTAL OFFSET
9:00 | 4 | REQUIRED VERTICAL OFFSET
6:00 | 3 | ALLOWABLE ERROR (+ OR -)
3:00 | -1
(G) | -5 | HORIZONTAL PARALLEL MISALIGNMENT
(H) | 0 | REQUIRED HORIZONTAL OFFSET
(J) | -5 | HORIZONTAL ERROR
| -2.5 | MOTOR MOVEMENT NEEDED
( - ) INDICATES THE MOTOR IS TOO FAR RIGHT OF THE COMPRESSOR OR PUMP
(+ ) INDICATES THE MOTOR IS TOO FAR LEFT OF THE COMPRESSOR OR PUMP
(K) | 3 | VERTICAL PARALLEL MISALIGNMENT
(L) | 0 | REQUIRED VERTICAL OFFSET
(M) | 3 | VERTICAL ERROR
| 1.5 | MOTOR MOVEMENT NEEDED (SHIMS)
( - ) READING INDICATES THE MOTOR IS LOW
( +) READING INDICATES THE MOTOR IS HIGH
(Q) ( + OR - ) | 0.002 | ALLOWABLE ERROR
ANGULAR ALIGNMENT
READINGS
12:00 | 0
9:00 | 2
6:00 | 1.5
3:00 | 0
REFERENCE DATA
ALLOWABLE ANGULAR ERROR ( + OR - ) |  |  | 0.002
DISTANCE BETWEEN FRONT AND REAR HOLD DOWN BOLTS |  |  | 36
DIAMETER OF COUPLING IN INCHES |  |  | 8
COUPLING RATIO |  |  | 4.5
(N) | -2 | HORIZONTAL ANGULAR MISALIGNMENT
| -9 | MOVEMENT NEEDED
( - ) READING INDICATES THE DEAD END OF THE MOTOR IS RIGHT OF THE CENTER LINE.
( + ) READING INDICATES THE DEAD END OF THE MOTOR IS LEFT OF THE CENTER LINE.
(P) | 1.5 | VERTICAL ANGULAR MISALIGNMENT
| 6.75 | SHIM NEEDED
( - ) READING INDICATES THE DEAD END OF MOTOR IS LOW
( + ) READING INDICATES THE DEAD END OF MOTOR IS HIGH
(R) | 0.002 | ( + OR -) ALLOWABLE ERROR
Notes:
Technician: