## Report
Measurement data
Filename |  |  |  | E315 CHILLER #8 (GACM117864)
Measurement date |  |  |  | 2017-11-28 20:53
Report generated from file |  |  |  | 8.2_hor_2017-11-28 20-53-00.5.Kevin Fraze.XML
Report generated date |  |  |  | 2017-12-14 11:53
Operator |  |  |  | Kevin Fraze
Measurement Program |  |  |  | EASY-LASER® Shaft Horizontal AX3
Measurement Unit |  |  |  | mils
Serial no. Display / detector(s) |  |  |  | 43278 / 43331 / 43305 / 0
Compressor Temperature |  |  |  | 139 F
Compressor Pressure |  |  |  | 72 PSIG
Distances |  | (Inch)
Coupling diameter |  | 8
SC |  | 2
SM |  | 4
M - MF1 |  | 14.1
MF1 - MF2 |  | 36
Machine data |  |  |  | Stationary Machine S |  | Movable Machine M
Name |  |  |  | Compressor |  | Motor
Movable pair of feet |  |  |  | 0 |  | 4
Locked pair of feet |  |  |  | 4 |  | 0
Softfoot measured |  |  |  | No |  | No
Thermal compensation |  |  |  | Stationary Machine S |  | Movable Machine M
Vertical offset | [5 empty] | + 1.250 mils (above Comp)
Horizontal offset | [5 empty] | 0
Vertical angle | [5 empty] | 0
Horizontal angle | [5 empty] | 0
Tolerance
Offset |  | + /- 6.000 mils |  |  | Angle | + / - 0.500 mils/Inch
Result Vertical
Result |  |  | Within tolerance
Offset | -8.000 mils |  | NO
Angle | 0.000 mils/Inch |  | YES
Feet values |  | (mils)
MF1 | -8
MF2 | -8
Result Horizontal
Result |  |  | Within tolerance
Offset | -11.500 mils |  | NO
Angle | -0.500 mils/Inch |  | YES
Feet values |  | (mils)
MF1 | -19.55
MF2 | -37.55
Notes:
All readings are pre-adjustment.
12/13/2017 - Motor was moved Hozitonally by jacking bolts & brought into tolerance for Horizontal Offset.
This will be verified and recorded when the Vertical Offset is adjusted.
Date: | 2017-12-14 |  |  | Sign: