## A
Johnson Controls Alignment Report
JOB: |  |  | Laser Alignment
EQUIPMENT # |  |  | Dial Indicator
LOCATION:
PARALLEL ALIGNMENT
| READINGS |  | REFERENCE DATA
12:00 | 0 | REQUIRED HORIZONTAL OFFSET | 0
9:00 | -4 | REQUIRED VERTICAL OFFSET | 1.25
6:00 | -12 | ALLOWABLE ERROR (+ OR -) | 0
3:00 | -8
(G) | -4 | HORIZONTAL PARALLEL MISALIGNMENT
(H) | 0 | REQUIRED HORIZONTAL OFFSET
(J) | -4 | HORIZONTAL ERROR
| -2 | MOTOR MOVEMENT NEEDED
( - ) INDICATES THE MOTOR IS TOO FAR RIGHT OF THE COMPRESSOR OR PUMP
(+ ) INDICATES THE MOTOR IS TOO FAR LEFT OF THE COMPRESSOR OR PUMP
(K) | -12 | VERTICAL PARALLEL MISALIGNMENT
(L) | 1.25 | REQUIRED VERTICAL OFFSET
(M) | -13.25 | VERTICAL ERROR
| -6.625 | MOTOR MOVEMENT NEEDED (SHIMS)
( - ) READING INDICATES THE MOTOR IS LOW
( +) READING INDICATES THE MOTOR IS HIGH
(Q) ( + OR - ) | 0.002 | ALLOWABLE ERROR
ANGULAR ALIGNMENT
READINGS
12:00 | 0
9:00 | 2
6:00 | 4
3:00 | 2
REFERENCE DATA
ALLOWABLE ANGULAR ERROR ( + OR - ) |  |  | 0.002
DISTANCE BETWEEN FRONT AND REAR HOLD DOWN BOLTS |  |  | 36
DIAMETER OF COUPLING IN INCHES |  |  | 8
COUPLING RATIO |  |  | 4.5
(N) | 0 | HORIZONTAL ANGULAR MISALIGNMENT
| 0 | MOVEMENT NEEDED
( - ) READING INDICATES THE DEAD END OF THE MOTOR IS RIGHT OF THE CENTER LINE.
( + ) READING INDICATES THE DEAD END OF THE MOTOR IS LEFT OF THE CENTER LINE.
(P) | 4 | VERTICAL ANGULAR MISALIGNMENT
| 18 | SHIM NEEDED
( - ) READING INDICATES THE DEAD END OF MOTOR IS LOW
( + ) READING INDICATES THE DEAD END OF MOTOR IS HIGH
(R) | 0.002 | ( + OR -) ALLOWABLE ERROR
Notes:
Technician: