## SSV MARCH
Due Date | Agreement Name | SSV SR Number | CH. HVY | CH. LT | M. HVY | M. LT | controls | TASKING
2017-03-30 | AI Dupont 2016-2021 PSA Connected Premium | 1-46429465636 | 7.5 |  |  |  |  | CONNECTED OPERATIONALS CH # 1, 3, 4
2017-03-30 | ASHLAND 2016-17 8167 | 1-46432123831 |  | 2 |  |  |  | OPER AIR COOLED SCROLL | Russ 3/3
2017-03-30 | ASHLAND 2016-17 8134 | 1-46432135427 |  | 4 |  |  |  | COMP REFRIGERANT MONITOR | Russ 3/3
2017-03-30 | ASHLAND 2016-17 8136 | 1-46432147291 |  | 2 |  |  |  | OPER AIR COOLED SCROLL | russ 3/1
2017-03-30 | ASHLAND 2016-17 8145 | 1-46432159230 |  | 3.5 |  | 5 |  | COMP CHILLER, WATER COOLED SCROLL, (ML) tube brushing
2017-03-30 | Astrazeneca 5 year PSA 2016-2021 | 1-46420490375 | 3 |  |  |  |  | OPERS WC, HIGH PRESS #5 AND LOW VOLTAGE VSD
2017-03-30 | AstraZeneca Packaged RTU PSA 2017-2021 rev2 | 1-46416343945 | 15 |  | 22.5 | 23 |  | (CH) COMPS AND OIL SAMPLES 5CH12-FGDC AND 5CH11-FGDC OPER 4CH1-IQA; (MH) COMPS HEATING AND COOLING 5 RTU UNITS 4AC7, 4AC8, 4AC9, 4AC10, 4AC11; (ML) COMPS HEATING AND COOLING 2 RTU UNITS 5HVAC3 AND 5HVAC4; COIL CLEANING 4 UNITS; OPERS ON 4 CONDENSING UNITS, OPER RTU
2017-03-30 | BASF DPP BLDG-2016 | 1-46434282448 | 2 |  |  |  |  | Oper - Chiller, WC, Single Comp Screw - 1
2017-03-30 | BASF SPECIALTY CHEMICALS-QA BLDG | 1-46430509078 | 2 |  |  |  |  | Oper - Chiller, WC, Single Comp Screw - 1
2017-03-30 | Bayhealth - Kent General Hospital -2016-17 | 1-46435117785 | 9 |  |  |  |  | OPERS ON 3 CHILLERS AND VSD
2017-03-30 | CDC 1 - 2016-17 | 1-46417843179 | 24.5 |  |  |  |  | CH 1A, 2A AND 3A COMP OIL AND REFRIG SAMPLES ; COMP ON VSD'S
2017-03-30 | CDC 2 - 2016-17 | 1-46416537502 | 10 |  |  |  |  | CH 3B COMP, OIL AND REFRIG SAMPLES, AND COMP ON VSD
2017-03-30 | CDC1 RTU 6 operationals | 1-46424810247 |  |  |  | 9.5 |  | 11 OPERS ON RTU'S, OPERS ON 8 VFD'S | king 3/7
2017-03-30 | CSC AHU Contract 2016-17 | 1-46436616862 |  |  | 2.5 | 23.3 |  | (MH) OPERS ON 2 VANE AXIAL FAN; OPERS ON 2 RTU'S; (ML) 1 AHU OPER AND FILTER CHANGE; OPERS AND FILTER CHANGES ON 8 AHUS; FILTER CHANGES ON 2 AHU VANE AXIALS
2017-03-30 | CSC Newark CRAC Units 2016-17 | 1-46436771226 |  |  |  | 188 |  | COMPS ON 94 CRACS
2017-03-30 | CSC Newark CT 2016-17 | 1-46434510982 |  |  | 4 |  |  | VIB ANALYSIS ON R CTWR-LG
2017-03-30 | Dupont Stine Haskell PSA - 2017 | 1-46425653765 | 24.75 |  |  | 60 |  | (CH) COMPS ON 4 CHILLERS WITH OIL SAMPLE AND 4 VSD; (ML) 4 TUBE BRUSHINGS
2017-03-30 | Graham Packaging - 2016-17 Year 1 | 1-46419405990 | 17.75 |  |  | 2.5 |  | (CH) CONNECTED COMP; COMP ON WC LOW PRESS AND VSD WITH OIL SAMPLE LEAK CHECK WITH COMP (4 HRS); (ML) COMPS ON 5 PUMPS
2017-03-30 | MCC JPM-2016-17 | 1-46417819383 | 12 |  |  |  |  | OPERS ON 4 CHILERS AND VSD'S DCCH
2017-03-30 | MCC JPM-2016-17 | 1-46417848999 | 6.75 | 9 |  |  |  | (CH) OPPERS 3 CHILLERS AND STARTERS; (CL) COMPS ON 3 COOLING TOWERS OPS
2017-03-30 | MMC WILMINGTON PSA 2016006G000000r49KvIAI | 1-46432300758 |  |  |  | 2.25 |  | COMP SPLIT SYSTEM WITH BELT AND FILTER CHANGE AND COIL CLEAN
2017-03-30 | Resolute 2017-18 | 1-46353441643 | 184
2017-03-30 | Tap Biosystems Year 3 | 1-46437753648 |  |  |  | 0.75 |  | 3 FILTER CHANGES
2017-03-30 | UNIVERSITY OF DELAWARE ECUP CHILLER 2016-17 | 1-46428005743 | 3.5 |  |  |  |  | ECUP OPER
2017-03-30 | WR Berkley Chiller PSA 2016-17 | 1-46430903153 | 4 | 20 |  | 32 |  | (CH) BLOCK HOURS??? (CL) COMPS ON 2 CHILLERS WITH OIL AND REFRIG SAMPLES; (ML) COIL CLEANINGS ON 2 UNITS
2017-03-30 | WR BERKLEY CONTROLS PSA- 2017 | 1-46429754572 |  |  |  |  | 8 | CONTROLS (south team)
2017-03-30 | Zacros Hedwin 2016-17 | 1-46428056739 |  |  | 9 | 86 |  | NEED TO PRINT SERVICE REPORT FOR KING'S NOTES AS TO WHAT WAS DONE.

## SSV FEB 2017
Due Date | Agreement Name | SSV SR Number | CH. HVY | CH. LT | M. HVY | M. LT | controls | TASKING
2016-11-30 | DOVER LIBRARY 2016-17 | 1-41547142105 |  |  |  |  | 4 | controls | 12/8 Not scheduled
2017-01-31 | DOVER LIBRARY 2016-17 | 1-42844512036 |  |  |  |  | 0.5 | ADX Software- Controls, Supervisory
2017-01-31 | ASTRAZENECA RTU | 1-45694251825 | 2 |  |  | 12.75 |  | (CH) Oper Air Cooled; (ML) 3 Comps RTU, 2 Comp Splits, 4 coil cleaning; 4 opers condens unit AC scroll;
2017-01-31 | ASHLAND 8145 | 1-45239855501 |  | 7.5 |  | 5 |  | (CL) COMP WC SCREW, OIL ANALYSIS AND SAMPLE; (ML) TUBE | 2/18 IS THIS DONE? USED 29 HRS SO FAR- OIL SAMPLES NOT DONE???
2017-02-28 | AI Dupont 2016-2021 PSA Connected Premium | 1-44646128573 | 15.5 |  |  | 32 |  | (CH) comp CH #4, comp VSD low volt, Comp Ch#2??; (ML) tube and gantry | In process 2/2-3 6 hrs to do high voltage starter comp/ 1 hr nxgen
2017-02-28 | ASHLAND 2016-17 8134 | 1-44608459498 | 5.5 |  |  | 12 |  | (CH) Comp on Carrier 23xl and oil sample/analysis; (ML) tube brushing
2017-02-28 | ASHLAND 2016-17 8100 | 1-44608538253 | 9.5 |  |  | 16 |  | (CH) Comp Trane, oil sample and anlaysis, LEAK CHECK (4 HRS); (ML) TUBE BRUSH | IS THIS DONE? USED 46 HRS. Note on comp that keith found leaks- premium chiller
2017-02-28 | ASHLAND 2016-17 8145 | 1-44608592282 |  |  |  | 5 |  | (ML) tube brushing only
2017-02-28 | ASHLAND 2016-17 8136A | 1-44608619210 | 4 |  |  |  |  | (CL) Refrig monitor comp - all are broken right?? 3 quotes to Dave in January - Bill | only one monitor is in good working order- completed. Quotes have been created to repair/replace
2017-02-28 | Astrazeneca 5 year PSA 2016-2021 | 1-44625164180 | 3 |  |  |  |  | (CH) Opers on VSD and WC High press chiller #4
2017-02-28 | BASF DPP BLDG-2016 | 1-44611561512 | 2 |  |  |  |  | (CH) Oper WC Screw #1 | 2/20 keith
2017-02-28 | BASF SPECIALTY CHEMICALS-QA BLDG | 1-44647027597 | 2 |  |  |  |  | (CH) Oper WC Screw #1 | 2/20 keith
2017-02-28 | Bayhealth - Kent General Hospital -2016-17 | 1-44648842479 | 9 |  |  |  |  | Opers on 3 chillers and low volt VSD
2017-02-28 | CDC 2 - 2016-17 | 1-44641182342 | 50 |  |  |  |  | comps on 6 chiller, vsd, oil sample, refrig samples | in process
2017-02-28 | Chemours Red Lion - 2016-17 | 1-44640276217 |  | 4 |  | 11 |  | (cl) OPERS ECR ROOM AND MAIN BLDG AC1; (ML) Opers on 3 packaged units, 2 AHUs; and 5 filter changes
2017-02-28 | DOVER LIBRARY 2016-17 | 1-44656865087 |  |  |  |  | 8 | PM visits- block hours
2017-02-28 | Dupont Stine Haskell PSA - 2017 | 1-44605070303 | 27 |  |  | 36 |  | (CH) Comps on 3 chillers and LV VSD, 3 oil and refrig samples; (ML) 3 tube brushinng
2017-02-28 | MCC JPM-2016-17 | 1-44654638427 | 15 |  |  |  |  | DCCH 4 COMPS WITH OIL AND REFRIG SAMPLES; COMP ON VSD
2017-02-28 | University of DE-Biotech 2016 | 1-44618487112 | 6 | 4 | 0.26 | 4.5 |  | (CH) OPER ON 2 W/C LOW PRES AND OPER HIGH VOL VSD; (CL) OPERS 2 TOWERS AND ONE A/C RECIP; (MH) 2 vsd oper s; (ML) opers on 7 condenser pumps, oper 3 cirulating pumps; opers on 2 crac units | 2/18 opers on 2 towers; opers vsd
2017-02-28 | UNIVERSITY OF DELAWARE ECUP CHILLER 2016-17 | 1-44611463924 | 3.5 | 4 |  |  |  | (CH) Ecup oper; (CL) Comp refrig monitor
2017-02-28 | Zacros Hedwin 2016-17 | 1-44614871912 |  | 12 | 3 | 37 |  | (CL) opers on 4 WC screw, opers on 4 cooling towers; (MH) opers on 3 RTU; (ML) Opers on 27 Gas unit heaters; Opers 2 process pumps; oper 2 condenser pumps; opers 7 circulating pumps, oper 2 chiller water pumps, oper 6 split syst, oper 21 RTU's | MH and ML in process 2/1-3
2017-02-28 | GREEN ROOM | 1-46413304089 |  | 5 |  |  |  | (CL) OPERS TOWER, AND 2 CHILLERS | RUSS 2/20
2017-02-28 | RESOLUTE | 1-46413240368 | 168
2017-02-28 | ASTRAZENECA PHARMACEUTICALS LP RTU | 1-45695402367 | 6 |  |  | 9.5 |  | (CH) 3 opers on AC scroll; (ML) 4 comps and coil clean RTU, 1 comp & coil clean Split; | Linford doing the ML on 2/3
|  |  | 326 | 29 | 3.26 | 163 | 8
| JCI BATTERY PLANT | MASTER CONTRACT | MC7EKL0005 |  |  |  |  | $11,000 (1 ylaa AND 1 yvaa AND 1 Solution unit XTO)
| DUPONT HOSPITAL FOR CHILDREN | 1-47432092689 | [5 empty] | chiller #4 e link issue
| DUPONT HOSPITAL FOR CHILDREN | 1-46538766782
| Ashland 8167 PSA | 1-46705782080 | [5 empty] | sensor
| 300 DELAWARE AVE | 1-45901727510 | 4 |  |  |  |  | PSA TRANSDUCER ISSUE
| UNIV OF DE - ECUP - MODEM REPAIR | [6 empty] | $650 IN MODEM.
| ASTRAZENECA | 1-46660986220 | [5 empty] | #5 ELINK
| BIOTECH PUMP CW PUMP1 | 1-45393130284 | fraze started it |  |  |  |  | 2175 ($2277 actual cost) | Condenser Pump #5: Due to pump shaft binding, Re-removed pump bearing assembly from volute. Removed and replaced both bearings. Cleaned and inspected all surfaces. Packed new bearings with Lithium Moly grease. Reassembled all parts, and installed new shaft seal. Discovered the following issues while proceeding with re-assembly: • Impeller spacer/washer and backing gasket for securing bolt was severely corroded and needs to be replaced. • Impeller rim runout is 0.006" when mounted on shaft and rotated. • Concrete anchors that secure metal pump base have come loose. • Piping and Pump volute seem to be cocked in a clockwise rotation making Pump and Motor alignment difficult. *Will order remaining rebuild parts not included with original order. And re-attempt assembly.

## TRAILING COSTS
SR Category | Bill to Account Name | Site Account Name | SR Number | Sub Status Category | Status Last Updated | Quoted NTE Amount | WIP Labor | WIP Material | WIP Subcontractor | WIP Other | Total WIP | comments | SR Description
Quoted | CAPITAL SCHOOL DISTRICT | WILLIAM HENRY MIDDLE SCHOOL | 1-37491979933 | Branch Status | 2016-08-25 10:51 | 883.2 | 308.28 | 19.67 | 0 | 27 | 354.95 | sent to brc 8/27 - SR 1-37555971521 OPENED FOR AIR VENT OR AIR BLEEDER-$315-- from Ferguson | Chemically clean condenser coils and furnish and install new air bleeder in chiller piping On chiller near the gym
Quoted | CRANSTON HEIGHTS FIRE COMPANY | CRANSTON HEIGHTS FIRE COMPANY | 1-37271106127 | Y | 2016-08-17 10:59 | 1032.49 | 231.21 | 0 | 0 | 27 | 258.21 | Johnstone supply costs to hit. | Furnish and install new condenser fan motor, blade and capacitor
Quoted | HOCKESSIN FIRE COMPANY | HOCKESSIN FIRE COMPANY | 1-37397332834 | Y | 2016-08-22 11:36 | 1403.8 | 616.57 | 0 | JOHNSTONE SUPPLY COSTS TO HIT. | 36 | 652.57 | Johnstone supply | Coat Room A/C Install emergency drain pan under unit. Mount and hang drain pan under unit. Relocate condensate pump lower to run drain from unit and pan into pump. Fill pans with water to check operations.
Quoted | THE CHEMOURS CANADA COMPANY | CHEMOURS COMPANY FC LLC - RED LION | 1-37116350965 | Y | 2016-08-11 20:03 | 17597.81 | 3819.85 | 2362.57 | 0 | 524.7 | 6707.12 | trailing labor and maybe material HOLDING SPOT SR IS 1-37644191418 | - Retrofit existing DDC controller in ECR rooftop unit with a FEC (+) controller. Replace existing sensors with JCI compatible devices. Reuse existing control wiring, dampers, actuators, valves, electrical components, etc. Replacement of any these items,
Quoted | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | 1-36763600243 | Y | 2016-08-01 11:40 | 12668 | 2211.91 | 3841.95 | 0 | 90 | 6143.86 | adjusted quote minus crane.;AND WRONG ECONOMIZER 1-37677350259 | Powerhouse BLDG Lockeroom A/C replacement. Furnish and install new 4 ton RTU York Model #J04ZFC00B4C1BAA1A1 and curb adapter. Lock out/tag out unit. Recover refrigerant charge and document. Crane lift and remove old unit. Crane lift new curb adap | adjusted quote minus crane. | Powerhouse BLDG Lockeroom A/C replacement. Furnish and install new 4 ton RTU York Model #J04ZFC00B4C1BAA1A1 and curb adapter. Lock out/tag out unit. Recover refrigerant charge and document. Crane lift and remove old unit. Crane lift new curb adap
|  | CSC NEWARK | 1-40655556042
|  | PROCTOR AND GAMBLE | 1-38496952862 | [8 empty] | NEED A CREDIT ON PART BEING RETURNED. RUSS INVENTORY (RMA 230163008- TRACKING FED EX 777322502179- NEED CREDIT FOR PART 371 01450 002 )
|  | Hockessin fire company | 1-42744701084 |  | 2016-11-29 20:46 | [6 empty] | Safety Clean should be applied - $250
|  | mcc | 1-42867322672

## PSA NOTES-PROBLEM JOBS
PSA NOTES:
STINE: USE MECHANIC LIGHT WHEN POSSIBLE. Maybe a change order? To correct chiller light and mechanic light.
Cokesbury - 2 psa repairs in three months.
Chestnut run - validate SDP as April 2017 is next visit.
BASF Tasking taking longer than expected. Foreman states that it is not realistic to do operationals in short period. Possible Change order.
Chestnut run 713 bldg No known issues at this time. Chiller Light labor planned - Chiller heavy actual. Change order? -
Zacros - CHILLERS 3 AND 4 ARE NOT RUNNING DUE TO SENSORS. We owe vibe analysis (July 2016) and opers (October 2016)
tasks that take much longer than NxGen gives - Ashland 8136A heat exchanger plate clean 15 min nxgen/ 32 hrs per foreman
Ashland 8136A heat exchanger plate clean 15 min nxgen/ 32 hrs per foreman- december 2016
AI Hospital High Voltage starter comp: NxGen = 60 min. Actual 4 hours
https://jll.okta.com/app/joneslanglasalle_360facility_1/exk19schmdcUrYgMZ0h8/sso/saml
Noteworthy jobs
VERIZON | 1-45537960458 | 1-41680937097 - CHRIS/KING JOB FROM OCTOBER 2016 (L&M)
*GO APPS ID: 9571** Problem: CRAC #2 has leaks in both circuits. Resolution: Johnson Controls proposes to repair leaks on circuit 1 and circuit 2 refrigerant piping. Circuit 1: Cut and remove leaking section of piping on condenser liquid connections. Replace relief valve. Also replace liquid line filter dryer and sticking solenoid valve and coil. Install new gaskets on king valve packing. Pressure check system again, pull vacuum and recharge system with 40 pounds of refrigerant R-22. Circuit 2: Cut and remove leaking section of piping on condenser liquid connections. Replace relief valve. Also replace liquid line filter dryer and sticking solenoid valve and coil. Install new gaskets on king valve packing. Pressure check system again, pull vacuum and recharge system with 40 pounds of refrigerant R-22 CRAC #2 Mfr: Air Flow Model #: AFY214A2-UD Serial #: P2YPD015 Found On: Leak Check SR#: 1-41250029641 Estimated Lead Time for Materials: In Stock Labor: $4,659.00 Materials: $3,198.80 Total: $7,857.80
CIGNA | 1-42842266721 | King was very efficient. Total hours allotted =24;- total hours used =16. Report out.
CDC1 | 1-43180488716 | H2 POWER EXHAUST FANN MOTOR - QUOTED $756. 1ST MOTOR INCORRECT ($176-NON-RETURNABLE) Second motor $400+ - additional labor to figure out motor voltage was incorrect.
FEB NOTEWORTHY
ASHLAND 8145 pm USED 29 HRS VS 12.5 NXGEN
ASHLAND 8134 PM'S USED 23 VS 17.5 NXGEN
ASHLAND 8100 PM'S USED 46 VS NXGEN 25.5
MCC JPM-2016-17 - used 22 hrs vs Nxgen 15
CDC2 PM'S

## north wip and warranty
SR Sub Type | Bill to Account Name | Site Account Name | SR Number | Billable Flag | SR Status | Quoted NTE Amount | WIP Labor | WIP Material | WIP Subcontractor | WIP Other | Total WIP | WIP Category | SR Description | Warranty Comment Date | Warranty Last Comment
Labor & Material | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | 1-46599898355 | Y | Scheduled |  | 223.74 | 369.01 | 0 | 4.5 | 597.25 | PSA | (PSA) CHLLER#1 PUMP VSD
Customer Satisfaction | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | 1-45901727510 | N | In Progress |  | 447.48 | 0 | 0 | 18 | 465.48 | PSA | (PSA) Both Chillers in alarm. Oil VFD and Transducer fault.
Customer Satisfaction | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | 1-47294836691 | N | Scheduled |  | 335.6 | 0 | 0 | 11 | 346.6 | PSA | Chiller #2 loss of current alarm.
Custom Quote | ASHLAND INC | ASHLAND BUILDING 8100 | 1-45920666164 | Y | Scheduled | 5451 | 1935.76 | 0 | 1266 | 36 | 3237.76 | coming back due to gaskets costs not incurred- midwest parts-Trane | Building 8100 Trane CVHF770 s/n L98C01705 Perform eddycurrent testing on all condenser and evaporator tubes. Lock out / tag out unit. Isolate and drain condenser and evaporator bundles. Remove condenser and evaporator heads. Brush clean all evaporat
Custom Quote | ASHLAND INC | ASHLAND BUILDING 8136A | 1-45920666670 | Y | Scheduled | 5928 | 2391.95 | 118.89 | 1565 | 67.5 | 4143.34 | sent to BRC | Building 8136A York m/n YTK7D6F1-CSH s/n GLGM046754 Perform eddycurrent testing on all condenser and evaporator tubes. Lock out / tag out unit. Isolate and drain condenser and evaporator bundles. Remove condenser and evaporator heads. Brush clean al
Customer Care | ASHLAND INC | ASHLAND INCORPORATED | 1-36321261099 | N | In Progress |  | 2493.95 | -296.02 | 0 | 117 | 2314.93 | Has WIP | Bldg. 8159 UPG WARRANTY-CLAIM #J382294 faulty compressor-ordering replacement compressor per John Walker s/n N1A6250678 J399804-2ND COMPRESSOR - claim not filed yet. need SI# and claim being built to deny due to 2 faulty claims back to back. working
Customer Satisfaction | BANK OF AMERICA PAYMENT PREP GROUP | BOA DE5-001 | 1-46753611814 | N | In Progress |  | 559.34 | 0 | 0 | 14.4 | 573.74 | sdp built- need to move once SR's are created- russ putting one hour on it. | HOLDING SPOT FOR PM'S UNTIL SDP IS BUILT
Customer Satisfaction | BANK OF AMERICA PAYMENT PREP GROUP | BOA DE5-002 | 1-46710593901 | N | In Progress |  | 615.27 | 0 | 0 | 16.2 | 631.47 | need product change order | HOLDING SPOT FOR PM'S UNTIL SDP IS BUILT.
Customer Satisfaction | BANK OF AMERICA PAYMENT PREP GROUP | BOA DE5-003 | 1-46711908680 | N | Scheduled |  | 615.27 | 0 | 0 | 28.8 | 644.07 | sdp built- need to move once SR's are created | HOLDING SPOT FOR PM'S UNTIL SDP IS BUILT
Labor & Material | BANK OF AMERICA PAYMENT PREP GROUP | BOA DE5-011 | 1-46540218339 | Y | In Progress |  | 2664.2 | 0 | 0 | 48.6 | 2712.8 | KK= I can follow up with the customer on Monday- kk | BOILER REPAIR
Warranty to Equipment | BUILDING SYSTEMS & SERVICES (BUY/RESELL) | BUILDING SYSTEMS AND SERVICES, INC | 1-47263644901 | N | Scheduled |  | 0 | 170.33 | 0 | 0 | 170.33 | Has WIP | BSS REQUESTED WARRANTY PER MARK SHETTLE AMTRAK- WORTH & CO S/N N1K6020728 M/N J06ZFN12B4A1BAA1A1 UPG CLAIM J486210
Customer Satisfaction | DELAWARE STATE UNIVERSITY | DELAWARE STATE UNIVERSIT | 1-46714096111 | N | Scheduled |  | 5824.4 | 122.32 | 0 | 333 | 6279.72 | PSA | Meeting and asset collection 2/13 (CK, JK) Asset collection 2/14 (CK, KEwing). Asset collection 2/17 (CK) Asset collection 2/20 (CK, KEwing, DAmes) Asset collection 2/21 (CK) Asset collection 2/22 (CK) Asset collection 2/24 (CK) 2/28 D. Naber- Beta
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47874641859 | Y | Scheduled | 1432.06 | 0 | 0 | 0 | 0 | 0 | not scheduled | E306 RTP Chilled Water Loop: Calculate appropriate System Fill Pressure based on height of highest coil and specific gravity of the Chilled Water. Isolate/Drain Expansion Tank. Increase Expansion Tank Bladder Pressure to System Fill Pressure with Nitr
Labor & Material | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47402231723 | Y | Scheduled |  | 91.02 | 113.6 | 0 | 0 | 204.62 | MOVED GRAINGER COSTS #10 MAINT (VALIDATE). AND Goodway 1-800-333-7467 x 6334 is LeShann in invoice dept. WAY BEHIND | (EMERG. PO 6501690015) Order Goodway Brushes fro tube cleaning.
Labor & Material | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47444087633 | Y | Scheduled |  | 364.08 | 554 | 0 | 13.5 | 931.58 | FRAZE-NEED QUOTE | Chiller #9 Condenser tube plugging.
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-46438155392 | Y | Scheduled | 4112.16 | 728.16 | 0 | 0 | 45 | 773.16 | NEED COSTS TO HIT | CHILLER #10 EDDY-CURRENT EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR & CONDENSER TUBES (1,582 TOTAL) FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED UPON COMPLETION. *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED AND BRUSHED BEFORE TECHNICIAN ARRIV
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47436369564 | Y | Scheduled | 988 | 546.13 | 0 | 0 | 13.5 | 559.63 | FRAZE-NEED COMMENTS | (6501697258) CHILLER #9 EVAPORATOR WATERBOX REPAIRS: CLEAN AND PREPARE TUBE SHEET DIVISION PLATE TRACKING FOR STEEL EPOXY COATING APPLY BELZONA 1121 "SUPER XL-METAL" (PURCHASED UNDER DUPONT PO#: 6501690015) TO FILL IN PITS AND GOUGING CLEAN UP AND
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47443336030 | Y | Scheduled | 4740.1 | 3003.69 | 93.67 | 0 | 126 | 3223.36 | FRAZE-NEED COMMENTS | (6501709952) Chiller #10 Annual Maintenance 2017 Remove Refrigerant Sample for Chemical Analysis Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filt
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47873229676 | Y | Scheduled | 1296.26 | 364.08 | 8.3 | 0 | 18 | 390.38 | FRAZE-NEED COMMENTS | (6501711947) CHILLER #10: Due to Refrigerant Leaks discovered on 03/03/2017 the following work is Recommended: Transfer entire R-134A charge to YORK Central Recovery Tank. Document weight of charge and calculated percentage loss based on design. P
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47953222455 | Y | Scheduled | 3950 | 546.12 | 0 | 0 | 38.34 | 584.46 | FRAZE-NEED COMMENTS | CHILLER #10 REFRIGERANT PIPING LEAK REPAIR: REPAIR OF THE FOLLOWING LEAKS FOUND ON 03/03/17: 1-1/2" THREADED LIQUID REFRIGERANT TEE FEEDING OIL COOLER COMP. OIL RESERVOIR EQUALIZING LINE 1/4 THREADED FLARE ELBOW CUT & DISMANTLE REFRIGERANT
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47954372704 | Y | Scheduled | 2601.37 | 182.04 | 1017.62 | 0 | 13.5 | 1213.16 | FRAZE-NEED COMMENTS | CHILLER #10 PRV SHAFT SEAL REPLACEMENT REPAIR OF THE FOLLOWING REFRIGERANT LEAK FOUND ON 03/03/17: COMPRESSOR PRE-ROTATION VANE SHAFT SEAL DISSMANTLE & REMOVE OLD SEAL ASSEMBLY FURNISH & INSTALL NEW SEAL ASSEMBLY WITH NEW ORINGS, GASKET, & FASTE
Warranty to Equipment | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | 1-46604691980 | N | Scheduled |  | 537.02 | 0 | 0 | -537.02 | 0 | Costs will flow overnight back in to NxGen WIP. | (claim updated and sent as complete 2/25) Model ylaa0070se46x Serial 11531c64654501 FREE COOLING ISSUES | 2017-03-09 | CHARGEDBACK PER BRANCH REQUEST.
Labor & Material | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | 1-47345766979 | Y | Scheduled |  | 1289.65 | 780.29 | 0 | 40.5 | 2110.44 | KK | 120 chiller Due: 24-Feb Desc: Chiller is down Svc Hrs: Right Now Access: Call site POC, need to fill out safety analysis Contact: Shawn 302-377-0771 Caller: Shawn 302-377-0771
Labor & Material | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | 1-47459196361 | Y | Scheduled |  | 2027.81 | 696.48 | 0 | 36 | 2760.29 | KK | SYSTEM 1 LEAK CHECK BLDG 120
Labor & Material | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | 1-47875218740 | Y | Scheduled |  | 1121.31 | 154.57 | 0 | 9 | 1284.88 | KK | Bldg 210N, Leak Check System 2
Custom Quote | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | 1-47714992937 | Y | Scheduled | 1723.4 | 0 | 67.21 | 0 | 0 | 67.21 | KK | DuPont Stine BLDG 190 New Chiller Mount and add temperature controller to unit enable circuit. Wire and test operation of new control
Custom Quote | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | 1-47863208363 | Y | Scheduled | 2653.99 | 0 | 157.35 | 0 | 0 | 157.35 | KK | DuPont Stine BLDG 215 Chiller #1 Replace Failed Oil Cooler TXV valve. Lock out tag out chiller. Isolate valve and remove TXV. Install new TXV with access port. Pull vacuum on line. Open valves and check for leaks. Start up chiller and check operat
Custom Quote | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | 1-47910259143 | Y | Scheduled | 11202.76 | 429.62 | 1760.68 | 0 | 9 | 2199.3 | KK | DuPont Stine BLDG 120 System #1 MO-99 Refrigerant Chiller Leak Repairs. Lock out tag out chiller. Repair leaking copper suction line by relief valves. Replace leaking compressor motor terminals. Replace leaking oil cooler sight glass. Pressurize sy
Labor & Material | EDGEWELL PERSONAL CARE BRANDS LLC | EDGEWELL PERSONAL CARE | 1-47310176595 | Y | Audit |  | 894.94 | 0 | 0 | 68.8 | 0 | MOVED TO 1-47873229521- sr closed | Chiller #3 running low line voltage.
Labor & Material | EDGEWELL PERSONAL CARE BRANDS LLC | EDGEWELL PERSONAL CARE | 1-47495273517 | Y | Scheduled |  | 0 | 100.87 | 0 | 0 | 0 | MOVED TO 1-47873229521-sr closed | CONTINUATION OF CHILLER #3 RUNNING LOW LINE VOLTAGE (1-47310176595)
Labor & Material | EDGEWELL PERSONAL CARE BRANDS LLC | EDGEWELL PERSONAL CARE | 1-47873229521 | Y | Scheduled |  | 894.94 | 0 | 0 | 68.8 | 2028 | sent to BRC ------PUT ALL TOGETHER VALIDATE MOVES AND INVOICE /CLOSE | Install customer supplied starter logic board on Chiller #3.
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | EMORY HILL REAL ESTATE SERVICES INC | 1-46705312394 | N | Scheduled |  | 19910.57 | 0 | 0 | -17834.37 | 2076.2 | Has WIP | PROJECT 7N28-0053-LABOR ONLY(DISCOVER COOLING TOWER) 12 READS WAY, NEW CASTLE.
Warranty to Equipment | GE AVIATION | GE AVIATION | 1-43184675622 | N | Scheduled |  | 984.31 | 0 | 0 | -984.31 | 0 | Costs will flow overnight back in to NxGen WIP. | (resent claim 2/25 and email to Tim) a sd claim 8K709001. as of 1/7 PROGRESS-INACTIVE, BUT NOT REVIEWED OR CLASSIFIED NO HEAT S/N TDDM104900 | 2017-03-09 | CHARGEDBACK PER BRANCH REQUEST.
Warranty to Equipment | GE AVIATION | GE AVIATION | 1-45383279350 | N | Scheduled |  | 551.21 | 0 | 0 | -551.21 | 0 | Costs will flow overnight back in to NxGen WIP. | (updated SD with info 2/25). CUSTOMER STATES NO HEAT. ENTER PROBLEM, CAUSE AND SOLUTION. | 2017-03-09 | CHARGEDBACK PER BRANCH REQUEST.
Custom Quote | JONES LANG LASALLE AMERICAS INC | MCC - JPM | 1-47166975432 | Y | Scheduled | 2763.4 | 1932.23 | 245 | 0 | 25.2 | 2202.43 | sent to BRC | (JLL PO 2156022) Johnson Controls Inc. will provide labor and material to perform the following; 1. Lockout tagout DCCT2 2. Drain oil into storage container. 3. Replace input shaft seal. 4. Reconnect coupling and align motor and gearbox with lazer a
Custom Quote | JONES LANG LASALLE AMERICAS INC | MCC - JPM | 1-47167004638 | Y | Audit | 3987 | 1480.8 | 184.89 | 0 | 25.2 | 1690.89 | BRC STATUS | (JLL PO 2156022) Johnson Controls Inc. will supply labor and material to perform the following DCCT4 REPLACE COUPLER ON MOTOR; 1. Lockout tagout cooling tower. 2. Remove old coupler connecting motor and gearbox. 3. Install new coupler. 4. Align motor
Custom Quote | HBS EAST SOUTH CENTRAL WEST | MCC OPS-1 - JPM | 1-42618642157 | Y | Scheduled | 5536 | 108.52 | 11.84 | 0 | 7.2 | 127.56 | never | Program Optiview panel, connect wiring in Optiview panel in data center chillers DCCH1, DCCH2, DCCH3, DCCH4, test operation of reset temperature controls.
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709323851 | Y | Scheduled | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | sent to BRC | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709324299 | Y | Scheduled | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | sent to BRC | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709327747 | Y | Scheduled | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | sent to BRC | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709328051 | Y | Scheduled | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | sent to BRC | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709328499 | Y | Scheduled | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | sent to BRC | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709336251 | Y | Scheduled | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | sent to BRC | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709336699 | Y | Scheduled | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | sent to BRC | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709348595 | Y | Scheduled | 349 | 126.17 | 0 | 0 | 0 | 126.17 | sent to BRC | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
Labor & Material | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE ALLEN LABS | 1-47889534596 | Y | Scheduled |  | 1566.15 | 1197.5 | 0 | 18.9 | 2782.55 | in process today | Emergency Service call for York Chiller down to be performed under Work Order 469057.
Labor & Material | NEWS JOURNAL COMPANY | WILMINGTON NEWS JOURNAL | 1-47420983445 | Y | Scheduled |  | 1454.28 | 0 | 0 | 9.9 | 1464.18 | done per russ- move to a quote??? - sent JDTR to JW | John Walker discussed issue with Craig M.

## north no wip
SR Sub Type | Bill to Account Name | Site Account Name | SR Number | Billable Flag | SR Status | Sub Status | Sub Status Category | Quoted NTE Amount | WIP Labor | WIP Material | WIP Subcontractor | WIP Other | Total WIP | WIP Category | SR Description | Warranty Comment Date | Warranty Last Comment
Condition A | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | 1-28106927932 | Y | Completed | Customer Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Condition A
Condition A | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | 1-28106928104 | Y | Open | Unscheduled | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Condition A
Labor & Material | ASHLAND INC | ASHLAND BUILDING 8100 | 1-43022929401 | Y | Scheduled | Pending Tech Acceptance | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | TRANE PURGE
PCAT Quoted | JCI US HVAC ES COMM SERV | ASTRAZENECA PHARMACEUTICALS LP | 1-32680697625 | Y | Open | Unscheduled | Branch Status | 1165 | 0 | 0 | 0 | 0 | 0 | No WIP | Start-up/PCAT Labor¦1-Day - UNIT TRAINING
PCAT Quoted | JCI US HVAC ES COMM SERV | ASTRAZENECA PHARMACEUTICALS LP | 1-32680697811 | Y | Scheduled | Tech Accepted | Branch Status | 2000 | 0 | 0 | 0 | 0 | 0 | No WIP | Start-up/PCAT Labor¦Humidifer cost repair-1/2 (UNIT STARTUP)
PCAT Quoted | JCI US HVAC ES COMM SERV | ASTRAZENECA PHARMACEUTICALS LP | 1-32680923007 | Y | Open | Unscheduled | Branch Status | 1400 | 0 | 0 | 0 | 0 | 0 | No WIP | Truck Based Team Executed¦2% - REPAIR (Belt, Pulley Change, Modify Belt Guard)
PCAT Quoted | JCI US HVAC ES COMM SERV | ATK BLDG C-33 | 1-40683561505 | Y | Open | Unscheduled | Branch Status | 1920 | 0 | 0 | 0 | 0 | 0 | No WIP | YCAL - Air Cooled Chiller - CH1¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2016
PCAT Quoted | JCI US HVAC ES COMM SERV | ATK BLDG C-33 | 1-42856793230 | Y | Open | Unscheduled | Branch Status | 1280 | 0 | 0 | 0 | 0 | 0 | No WIP | DX Air Cooled Condensing Units - CU-1¦Start up/PCAT - Branch: Delmarva - 0260 in 2016
ROC Applications | BAYHEALTH MEDICAL KENT CAMPUS | BAYHEALTH MEDICAL KENT CAMPUS | 1-45532648380 | Y | Scheduled | Pending Tech Acceptance | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Operating Alarm ROC alarm / Acc. # 5364-7016-602925/ 650/ SEWM592210 To place a disregard for this or any other signal, call the ROC at 800-753-4524 Opt. 1 and supply the operator with the Acct Number listed above 01/11/2017 08:17:46 Chiller 2 Stopped
Labor & Material | BAYHEALTH MEDICAL KENT CAMPUS | BAYHEALTH MEDICAL KENT CAMPUS | 1-35733786885 | Y | Approved (Internal) | Approved (Internal) | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | DO NOT BILL BAY HEALTH. THIS WAS FROM QUOTED JOB 1-35402627134. TRAILING COSTS WILL HAVE TO GO BACK.
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | CDC1 - JONES LANG LASALLE - JPM | 1-32327094311 | N | Scheduled | Tech Accepted | Branch Status |  | 34467.41 | 443.01 | 0 | -34910.42 | 0 | No WIP | Project #6N280077 (Please post labor only - NO material orders) CDC EXHAUST
Labor & Material | JONES LANG LASALLE AMERICAS INC | CDC1 - JONES LANG LASALLE - JPM | 1-45064355272 | Y | Scheduled | Tech Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | JPMC REQUEST ID 5340049: WC 3A Oil filter leak on service valve.
Custom Quote | JONES LANG LASALLE AMERICAS INC | CDC1 - JONES LANG LASALLE - JPM | 1-42983053543 | Y | Open | Unscheduled | Branch Status | 500 | 0 | 0 | 0 | 0 | 0 | No WIP | Customer Work Order #25837981-1 RTU-3 Sensor Fail Alarm Checked sensor failure problem on unit RTU-3. Found unit was configured for 4 stages of cooling and unit has only one stage. Configured unit properly. Unit stayed in dehumidification mode.
Material Only Quote | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | 1-46632635859 | Y | Scheduled | Pending Tech Acceptance | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | (NEED request id and work order) MATERIAL ONLY SR- 155 LBS OR REFRIGERANT PER KEVIN KELLY
Labor & Material | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | 1-45669372938 | Y | Scheduled | Tech Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Chiller 3B experiencing Proof of Run Fault.
Labor & Material | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | 1-45677493703 | Y | Open | NSA Priority | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | JPMC Request ID: N/A Call Center Reference #: 27816852-1 NTE: $500 Due: 1/17/2017 Desc: Provide a tech to investigate a loss of proof of chiller running. Svc Hrs: N/A Access: N/A Contact: Jamie Powers Caller: Email
Labor & Material | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | 1-46538281675 | Y | Scheduled | Pending Tech Acceptance | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | CHILLER 2A SIGHT GLASS REPAIR KEVIN PROVIDED QUOTE TO DAN LAZCO AWAITING PO/WO#
Custom Quote | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | 1-29332670721 | Y | Pending Adjustment | Pending Adjustment | Branch Status | 11904.78 | 0 | 0 | 0 | 0 | 0 | No WIP | JCI provided Training to CDC2. Course 2102
Custom Quote | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | 1-43296624880 | Y | Pending Adjustment | Pending Adjustment | Branch Status | 8626.8 | 0 | 0 | 0 | 0 | 0 | No WIP | CDC-2 Chiller 1B Leaking Oil Sight Glass Repair. (JPMC WO 27497175-1/ REQUEST ID 5271383) Lock out tag out chiller. Recover refrigerant charge. Remove oil and dispose off. Replace leaking oil sight glass and "O" rings. Install new sight glass and "
Custom Quote | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | 1-46760131188 | Y | Open | Unscheduled | Branch Status | 10448.87 | 0 | 0 | 0 | 0 | 0 | No WIP | CDC-2 Chiller 2A Leaking Oil Sight Glass Repair and "O" ring replacement Lock out tag out chiller. Recover refrigerant charge. Remove oil and dispose of. Replace leaking oil sight glass and "O" rings. While charge is out of machine we will replace
Custom Quote | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | 1-47273019847 | Y | Scheduled | Tech Accepted | Branch Status | 2103.57 | 0 | 0 | 0 | 0 | 0 | No WIP | (JLL PO 2274991) CDC-2 Chiller 1B VSD Fluid Replacement Lock out tag out vsd. Drain vsd fluid and remove all tubing. Install new tubing and fill with new drive fluid Labor = $147.00 @ 8 hrs. = $1,176.00 Material (3) VSD Fluid = $782.57 T
Custom Quote | EAST COAST PLUMBING & HVAC INC | COUNCIL OF THE DEVON | 1-36622889549 | Y | Open | Unscheduled | Branch Status | 57689 | 0 | 0 | 0 | 0 | 0 | No WIP | Repairs to York YT Chiller m/n YTG3A3B2-CGHS s/n GMLM143031 Mobilize all tools and equipment. Lock out / tag out unit. Recover, weigh, and store entire refrigerant charge. Disconnect motor wiring and compressor coupling. Set up rigging and remove com
Custom Quote | EAST COAST PLUMBING & HVAC INC | COUNCIL OF THE DEVON | 1-36630502193 | Y | Open | Unscheduled | Branch Status | 57689 | 0 | 0 | 0 | 0 | 0 | No WIP | Repairs to York YT Chiller m/n YTG3A3B2-CGHS s/n GMLM143031 Mobilize all tools and equipment. Lock out / tag out unit. Recover, weigh, and store entire refrigerant charge. Disconnect motor wiring and compressor coupling. Set up rigging and remove com
Material Only Quote | CBRE GWS LLC CSC | CSC NEWARK | 1-47974511134 | Y | Scheduled | Tech Accepted | Branch Status | 481.06 | 0 | 0 | 0 | 0 | 0 | No WIP | (WO C128923) Materials Only: Johnson Controls is to furnish qty-2 replacement fan motors for unit heaters in stairwells. Shipping included.
Labor & Material | CBRE GWS LLC CSC | CSC NEWARK | 1-45474073199 | Y | Scheduled | Tech On Site | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Two stairwell electric unit heaters, wall mounted, not working (Norman Marks).
Shared Resource to Projects | DFAS-VD/L1 F67100 LIMESTONE | DELAWARE AIR NATIONAL GUARD | 1-45659788401 | N | Scheduled | Tech On Site | Branch Status |  | 629.96 | 281.91 | 0 | -911.87 | 0 | No WIP | WARRANTY TO PROJECT
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | 1-27605896846 | N | Scheduled | Tech Accepted | Branch Status |  | 54940.74 | 591.09 | 0 | -55531.83 | 0 | No WIP | Project #5N280103 (labor only) VRF install
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | 1-32234168004 | N | Scheduled | Tech Accepted | Branch Status |  | 1596.82 | 0 | 0 | -1596.82 | 0 | No WIP | Project #5N280104 (labor only) Controls
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | 1-33673837211 | N | Scheduled | Tech Accepted | Branch Status |  | 56845.51 | 873.58 | 0 | -57719.09 | 0 | No WIP | DANG BLDG 2902 Project #5N280107
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | 1-38501911211 | N | Scheduled | Tech Accepted | Branch Status |  | 35905.59 | 526.95 | 0 | -36432.54 | 0 | No WIP | PROJECT#6N28-0164; Veterans Design and Construction.
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | 1-43440239875 | N | Scheduled | Tech Accepted | Branch Status |  | 708.7 | 0 | 0 | -708.7 | 0 | No WIP | DAIKIN WARRANTY ISSUE - NEED MODEL AND SERIAL NUMBER
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | 1-47280239011 | N | Scheduled | Tech Accepted | Branch Status |  | 439.39 | 4.7 | 0 | -444.09 | 0 | No WIP | Daikin indoor fan making loud noise when running.
Custom Quote | NORTHEAST UTILITIES SYSTEMS | DELAWARE SOLID WASTE AUTHORITY | 1-43411666964 | Y | Open | Unscheduled | Branch Status | 3235 | 0 | 0 | 0 | 0 | 0 | No WIP | York m/n YCAL0074EB46X s/n RHPM012366 Recover / reclaim current 407c refrigerant charge from circuit 2. Remove leaking relief valve on discharge line. Furnish and nstall QTY-1 discharge relief valve on circuit 2 discharge line. Pressure test syst
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | DISCOVER FINANCIAL SERVICES | 1-47831404653 | N | Scheduled | Pending Tech Acceptance | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | COOLING TOWER ISSUE
Not To Exceed | E I DUPONT | DUPONT CHESTNUT RUN | 1-41585574848 | Y | Open | Unscheduled | Branch Status | 3891.73 | 0 | 0 | 0 | 0 | 0 | No WIP | Johnson Controls Inc. will provide labor and material to perform the following; Building 713 Model number YLAA0115 Serial number 2GYM017106 1. Lockout system 1. 2. Remove refrigerant from system 1 and store in recovery tanks, weigh refrigerant recovered a
Custom Quote | E I DUPONT | DUPONT CHESTNUT RUN | 1-35209755059 | Y | Open | Unscheduled | Branch Status | 2920.85 | 0 | 0 | 0 | 0 | 0 | No WIP | York chiller model ylaa0115 serial 2gym017106. Remove leaving chilled water sensor and replace with new. Part # 025-29964-000f. Check operation of new sensor. System 2 recover remaining r410a , and pressure test with nitrogen. Evacuate and charge with
Custom Quote | E I DUPONT | DUPONT CHESTNUT RUN | 1-37481561411 | Y | Open | Unscheduled | Branch Status | 9481 | 0 | 0 | 0 | 0 | 0 | No WIP | Building #713 Chiller m/n YLAA0115SE46XCADBTCAX s/n 2GYM017106 Furnish and replace qty-1 leaking condenser coil on circuit #2. Lock out / tag out all energy sources. Recover and dispose of old refrigerant charge. Disconnect piping and remove old coi
Custom Quote | E I DUPONT | DUPONT CHESTNUT RUN | 1-37495128439 | Y | Pending Adjustment | Pending Adjustment | Branch Status | 2959 | 0 | 0 | 0 | 0 | 0 | No WIP | Troubleshoot VFD Fault. Ycaa0275/ 2dym015748 Remove and replace bleed down resistors on chiller 1 drive that are causing trouble faults on dc bus. Test drive operation. Labor 18 hrs @ $146.72 Parts. $318.00
Labor & Material | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47405246199 | Y | Scheduled | Tech On Site | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | (temporary holding spot for #9 Waterbox repair under PO 6501697258- NEED QUOTE)
Customer Satisfaction | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-43713008400 | N | Scheduled | Tech Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | RUPTURED DISC REPAIR - MOVING TO QUOTE 1-K2OOT6G WHEN RAUL GETS PO. Temporary holding spot for Mr. Kevin Fraze.
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-36028109391 | Y | Pending Adjustment | Pending Adjustment | Branch Status | 2099.2 | 0 | 0 | 0 | 0 | 0 | No WIP | ABSORBER #2 FURNISH 18 New PALL Bromide Solution FILTERS to REPLENISH Supply onsite. (6 Filters per Changeout) REMOVE and REPLACE current clogged Filters CLEAN out Canister EVACUATE and RETURN to Service
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-46718363513 | Y | Open | Unscheduled | Branch Status | 8699.09 | 0 | 0 | 0 | 0 | 0 | No WIP | CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4.975ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: TR
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-46719052659 | Y | Open | Unscheduled | Branch Status | 8699.09 | 0 | 0 | 0 | 0 | 0 | No WIP | CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4.975ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: TR
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47874641859 | Y | Scheduled | Tech Accepted | Branch Status | 1432.06 | 0 | 0 | 0 | 0 | 0 | No WIP | E306 RTP Chilled Water Loop: Calculate appropriate System Fill Pressure based on height of highest coil and specific gravity of the Chilled Water. Isolate/Drain Expansion Tank. Increase Expansion Tank Bladder Pressure to System Fill Pressure with Nitr
Shared Resource to Projects | NEMOURS FOUNDATION | DUPONT HOSPITAL FOR CHILDREN | 1-29002126551 | N | In Progress | Returning For Completion | Branch Status |  | 52274.33 | 1316.79 | 0 | -53591.12 | 0 | No WIP | Project #6N280057
ROC Applications | NEMOURS FOUNDATION | DUPONT HOSPITAL FOR CHILDREN | 1-32802135464 | Y | Open | Unscheduled | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Connected Services Installation
Custom Quote | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | 1-46898395673 | Y | Scheduled | Pending Arrival | Branch Status | 8358 | 0 | 0 | 0 | 0 | 0 | No WIP | BLDG #200 Chiller #1 and #2 Eddycurrent Testing York Model #YKDCDRQ4-CJGS Lock out/tag out chiller. Isolate and drain down condenser and evaporator bundles Store glycol form evaporator into drums. Remove heads and mechanically brush clean all tub
PCAT Quoted | JCI US HVAC ES COMM SERV | EI DUPONT DE NEMOURS & CO | 1-46708999753 | Y | Open | Unscheduled | Branch Status | 583 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: 3 VFD (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | EI DUPONT DE NEMOURS & CO | 1-46709000201 | Y | Open | Unscheduled | Branch Status | 583 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: 3 VFD (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | EI DUPONT DE NEMOURS & CO | 1-46709000649 | Y | Open | Unscheduled | Branch Status | 583 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: 3 VFD (Year of Startup: 2016)
Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | HEDWIN CORPORATION - NEWARK DE | 1-43300943355 | N | Scheduled | Tech Accepted | Branch Status |  | 8296.61 | 200.81 | 0 | -8497.42 | 0 | No WIP | LABOR ONLY. TO PURCHASE PARTS, USE 7N28-0038
Custom Quote | ZACROS AMERICA INC | HEDWIN CORPORATION - NEWARK DE | 1-47407296650 | Y | Open | Unscheduled | Branch Status | 1421 | 0 | 0 | 0 | 0 | 0 | No WIP | RTU #23 Carrier m/n 48TME008-A-601 s/n 0405G30410 Repair leak on discharge line of compressr. Reclaim and remove refrigerant from circuit #2. Pressure test system. Evacuate and perform a vacuum hold test. Recharge system with reclaimed refrigerant an
Customer Satisfaction |  | HOWARD R. YOUNG CORRECTIONAL INSTITUTION | 1-35456691111 | N | Scheduled | Pending Tech Acceptance | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Howard Young - Chiller - Failed suction pressure transducer for circuit 1 & 2 Problem: Failure on Circuit 1 and 2 Cause: Failed suction pressure transducer Resolution: Replace pressure transducer
Custom Quote | ID GRIFFITH | I D GRIFFITH INC - WILMINGTON | 1-47948959072 | Y | Scheduled | Tech Accepted | Branch Status | 9833 | 0 | 0 | 0 | 0 | 0 | No WIP | CDC-1 Bear, DE Provide qty-40 hrs of technician labor to test and commission RTU Power Exhaust systems and VFD's. Also provide qty-10 hrs labor on a Saturday to perfrom testing and verification.
PCAT Quoted | JCI US HVAC ES COMM SERV | JCI BATTERY DIVISION | 1-41281623381 | Y | Open | Unscheduled | Branch Status | 1320 | 0 | 0 | 0 | 0 | 0 | No WIP | YLAA - Air Cooled Scroll Chiller - ACCH110¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2017
Labor & Material | M DAVIS & SONS INC | JCI BATTERY DIVISION | 1-47812307187 | Y | Scheduled | Tech Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Jeff Lidke (302) 893-8007 of M Davis stated while pulling wires for Chiller install, a wire came in contact with the board. Request to replace board and inspect board on second chiller.
PCAT Quoted | JCI US HVAC ES COMM SERV | KRAFT HEINZ DOVER, DE | 1-46711468484 | Y | Open | Unscheduled | Branch Status | 500 | 0 | 0 | 0 | 0 | 0 | No WIP | Solution XTI - AHU-021R-384¦Field Labor (except PCAT) - Factory Startup
Labor & Material | JONES LANG LASALLE AMERICAS INC | MCC - JPM | 1-45949176549 | Y | Scheduled | Tech Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | EDDY CURRENT TESTING - COSTS NEED TO GO BACK TO SR 1-42867322672 THAT WAS BILLED ON 1/26.
Custom Quote | JONES LANG LASALLE AMERICAS INC | MCC - JPM | 1-47885260543 | Y | Scheduled | Tech Accepted | Branch Status | 11386 | 0 | 0 | 0 | 0 | 0 | No WIP | (JLL PO 2287094) MCC OPS-3 Cooling Tower. Ceramic Cooling Tower Co. M/n C1130 Install qty-1 customer furnished tower gearbox. Install qty-1 customer furnished tower fan motor. Lock out / tag out all energy sources. Disassemble tower gearbox coupl
Custom Quote | JONES LANG LASALLE AMERICAS INC | MCC - JPM | 1-47942847625 | Y | Scheduled | Tech Accepted | Branch Status | 395.85 | 0 | 0 | 0 | 0 | 0 | No WIP | (JLL WO28491742-1) Materials Only. Furnish qty-1 new PX110 Coupling insert for OPS Tower #2. Freight included. Pricing per JLL / JCI Contract Materials: qty-1 coupling insert $319.39 Overnight Freight $76.46 Total: $395.85
Labor & Material | JONES LANG LASALLE AMERICAS INC | MCC OPS-1 - JPM | 1-45595519441 | Y | Scheduled | Tech Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | WO: 27780679-1 JPMC REQ ID: 5390752 JCI TO INVESTIGATE OPERATIONS CENTER CHILLER 2 EXCESSIVE PURGE/ HIGH CONDENSING PRESSURE
Custom Quote | JONES LANG LASALLE AMERICAS INC | MCC OPS-1 - JPM | 1-47324367334 | Y | Scheduled | Tech Accepted | Branch Status | 25123.79 | 0 | 0 | 0 | 0 | 0 | No WIP | (2276599) Clean cooling towers for OPSCT1, OPSCT2, and OPSCT3. Provide Vacuum Truck service and labor to clean the OPS Cooling Towers. Pricing per JLL / JCI agreement.
Custom Quote | PROCTER & GAMBLE | PROCTOR & GAMBLE | 1-34182431774 | Y | Approved (Internal) | Approved (Internal) | Branch Status | 2450 | 0 | 0 | 0 | 0 | 0 | No WIP | Provide HVAC service on a T&M basis 5-10-16.
Custom Quote | PROCTER & GAMBLE | PROCTOR & GAMBLE | 1-47885111808 | Y | Scheduled | Tech Accepted | Branch Status | 7782 | 0 | 0 | 0 | 0 | 0 | No WIP | Chiller "B" m/n YTC3P3B2-CJD s/n YATM453436 Furnish and install qty-1 new carbon burting disk to replace defective Vent Guard Assembly. Lock out / tag out chiller. Recover, store, and weigh entire refrigerant charge. Disassemble old Vent Guard as
Custom Quote | PROCTER & GAMBLE | PROCTOR & GAMBLE | 1-47885260814 | Y | Scheduled | Tech Accepted | Branch Status | 9255 | 0 | 0 | 0 | 0 | 0 | No WIP | P&G Cooling Tower #5 Install customer supplied bearings on cooling tower. Lock out / tag out tower. Furnish install plywood across tower fill to prevent damage. Remove belts and fan pulley. Remove fan blade assembly. Remove shaft and bearings and
Labor & Material | RESOLUTE INDUSTRIAL | RESOLUTE INDUSTRIAL - DE | 1-45596708966 | Y | Scheduled | Tech Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Overtime requested by customer. 01/13-14/2017
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-41637583764 | Y | Open | Unscheduled | Branch Status | 2640 | 0 | 0 | 0 | 0 | 0 | No WIP | YLAA - Air Cooled Scroll Chiller - CH-1¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2017
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-41637675924 | Y | Open | Unscheduled | Branch Status | 2640 | 0 | 0 | 0 | 0 | 0 | No WIP | YLAA - Air Cooled Scroll Chiller - CH-2¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2017
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709335803 | Y | Scheduled | Tech Accepted | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709348147 | Y | Scheduled | Tech Accepted | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709357043 | Y | Scheduled | Tech Accepted | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | 1-46709357491 | Y | Scheduled | Tech Accepted | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
PCAT Quoted | JCI US HVAC ES COMM SERV | SEARS PRICES CORNER | 1-47156712557 | Y | Open | Unscheduled | Branch Status | 304 | 0 | 0 | 0 | 0 | 0 | No WIP | YCWL - Water Cooled Scroll Chiller - CH-2¦Connectivity - Connectivity - BACnet, Commissioning Labor, Installation Year: 2016
PCAT Quoted | JCI US HVAC ES COMM SERV | SEARS PRICES CORNER | 1-47156902126 | Y | Open | Unscheduled | Branch Status | 304 | 0 | 0 | 0 | 0 | 0 | No WIP | YCWL - Water Cooled Scroll Chiller - CH-2¦Connectivity - Connectivity - BACnet, Commissioning Labor, Installation Year: 2016
PCAT Quoted | JCI US HVAC ES COMM SERV | SEARS PRICES CORNER | 1-47156902605 | Y | Open | Unscheduled | Branch Status | 1900 | 0 | 0 | 0 | 0 | 0 | No WIP | YCWL - Water Cooled Scroll Chiller - CH-2¦Start up/PCAT - Branch: Philadelphia Service - 0607, Tier: 10 in 2016
PCAT Quoted | JCI US HVAC ES COMM SERV | SEARS PRICES CORNER | 1-47156903064 | Y | Open | Unscheduled | Branch Status | 1900 | 0 | 0 | 0 | 0 | 0 | No WIP | YCWL - Water Cooled Scroll Chiller - CH-2¦Start up/PCAT - Branch: Philadelphia Service - 0607, Tier: 10 in 2016
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-41212886021 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4266-452322/ / SET00108D0429DF Timestamp 10/11/2016 09:05:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-41362501991 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4408-464271/ / SET00108D0429DF Timestamp 10/18/2016 08:51:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-41441689859 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4457-468722/ / SET00108D0429DF Timestamp 10/21/2016 09:09:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-41520576322 | Y | Scheduled | Tech Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4495-474139/ / SET00108D0429DF Timestamp 10/25/2016 09:28:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-41915747637 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4558-499467/ / SET00108D0429DF Timestamp 11/09/2016 08:58:00 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-42119852862 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4594-503470/ / SET00108D0429DF Timestamp 11/12/2016 09:16:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-42426422070 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4625-508092/ / SET00108D0429DF Timestamp 11/15/2016 09:34:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-42836944625 | Y | Awaiting Internal Approval | Awaiting Internal Approval | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4743-535746/ / SET00108D0429DF Timestamp 12/01/2016 10:05:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-45876110740 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4898-625017/ / SET00108D0429DF Timestamp 01/25/2017 11:30:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-46604456418 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4943-646664/ / SET00108D0429DF Timestamp 02/08/2017 11:59:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-46684861701 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-4976-652522/ / SET00108D0429DF Timestamp 02/11/2017 12:17:00 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-46760357657 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-5009-656302/ / SET00108D0429DF Timestamp 02/14/2017 12:35:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-47714549796 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-5077-677877/ / SET00108D0429DF Timestamp 03/01/2017 13:05:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
ROC Applications | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | 1-47851580982 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 5161-5116-683495/ / SET00108D0429DF Timestamp 03/04/2017 13:23:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
PCAT Quoted | JCI US HVAC ES COMM SERV | UNIVERSITY OF DELAWARE00514773 | 1-34537671977 | Y | Pending Adjustment | Pending Adjustment | Branch Status | 960 | 0 | 0 | 0 | 0 | 0 | No WIP | DX Air Cooled Condensing Units - ACC-1_2¦Start up/PCAT - Branch: Delmarva - 0260 in 2016 SN 11531E64855064
PCAT Quoted | JCI US HVAC ES COMM SERV | USPS NEW CASTLE | 1-43730886575 | Y | Open | Unscheduled | Branch Status | 4166 | 0 | 0 | 0 | 0 | 0 | No WIP | YMC Chiller - CH-1¦Start up/PCAT - Branch: Philadelphia Service - 0607 in 2017¦Field Commissioning of Smart Chiller Equip Board
Labor & Material | CAPITAL SCHOOL DISTRICT | WILLIAM HENRY MIDDLE SCHOOL | 1-37555971521 | Y | Scheduled | Tech Accepted | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | HOLDING SPOT FOR POSSIBLE TRAILING COSTS FROM SR 1-37491979933. LOOKING FOR AIR BLEEDER OR AIR VENT 8/24 COBERHL ACTIVITY 1-H7NO8IH

## FRAZE SHEET
SR Sub Type | Bill to Account Name | Site Account Name | SR Number | Billable Flag | SR Status | Quoted NTE Amount | WIP Labor | WIP Material | WIP Subcontractor | WIP Other | Total WIP | WIP Category | SR Description | Warranty Comment Date | Warranty Last Comment
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47874641859 | Y | Scheduled | 1432.06 | 0 | 0 | 0 | 0 | 0 | not scheduled | E306 RTP Chilled Water Loop: Calculate appropriate System Fill Pressure based on height of highest coil and specific gravity of the Chilled Water. Isolate/Drain Expansion Tank. Increase Expansion Tank Bladder Pressure to System Fill Pressure with Nitr
Labor & Material | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47402231723 | Y | Scheduled |  | 91.02 | 113.6 | 0 | 0 | 204.62 | MOVED GRAINGER COSTS #10 MAINT (VALIDATE). AND Goodway 1-800-333-7467 x 6334 is LeShann in invoice dept. WAY BEHIND | (EMERG. PO 6501690015) Order Goodway Brushes fro tube cleaning.
Labor & Material | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47444087633 | Y | Scheduled |  | 364.08 | 554 | 0 | 13.5 | 931.58 | FRAZE-QUOTE | Chiller #9 Condenser tube plugging.
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-46438155392 | Y | Scheduled | 4112.16 | 728.16 | 0 | 0 | 45 | 773.16 | in process | CHILLER #10 EDDY-CURRENT EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR & CONDENSER TUBES (1,582 TOTAL) FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED UPON COMPLETION. *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED AND BRUSHED BEFORE TECHNICIAN ARRIV
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47436369564 | Y | Scheduled | 988 | 546.13 | 0 | 0 | 13.5 | 559.63 | FRAZE-NEED COMMENTS- | (6501697258) CHILLER #9 EVAPORATOR WATERBOX REPAIRS: CLEAN AND PREPARE TUBE SHEET DIVISION PLATE TRACKING FOR STEEL EPOXY COATING APPLY BELZONA 1121 "SUPER XL-METAL" (PURCHASED UNDER DUPONT PO#: 6501690015) TO FILL IN PITS AND GOUGING CLEAN UP AND
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47443336030 | Y | Scheduled | 4740.1 | 3003.69 | 93.67 | 0 | 126 | 3223.36 | FRAZE-NEED COMMENTS | (6501709952) Chiller #10 Annual Maintenance 2017 Remove Refrigerant Sample for Chemical Analysis Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filt
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47873229676 | Y | Scheduled | 1296.26 | 364.08 | 8.3 | 0 | 18 | 390.38 | FRAZE-NEED COMMENTS | (6501711947) CHILLER #10: Due to Refrigerant Leaks discovered on 03/03/2017 the following work is Recommended: Transfer entire R-134A charge to YORK Central Recovery Tank. Document weight of charge and calculated percentage loss based on design. P
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47953222455 | Y | Scheduled | 3950 | 546.12 | 0 | 0 | 38.34 | 584.46 | FRAZE-NEED COMMENTS | CHILLER #10 REFRIGERANT PIPING LEAK REPAIR: REPAIR OF THE FOLLOWING LEAKS FOUND ON 03/03/17: 1-1/2" THREADED LIQUID REFRIGERANT TEE FEEDING OIL COOLER COMP. OIL RESERVOIR EQUALIZING LINE 1/4 THREADED FLARE ELBOW CUT & DISMANTLE REFRIGERANT
Custom Quote | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | 1-47954372704 | Y | Scheduled | 2601.37 | 182.04 | 1017.62 | 0 | 13.5 | 1213.16 | FRAZE-NEED COMMENTS | CHILLER #10 PRV SHAFT SEAL REPLACEMENT REPAIR OF THE FOLLOWING REFRIGERANT LEAK FOUND ON 03/03/17: COMPRESSOR PRE-ROTATION VANE SHAFT SEAL DISSMANTLE & REMOVE OLD SEAL ASSEMBLY FURNISH & INSTALL NEW SEAL ASSEMBLY WITH NEW ORINGS, GASKET, & FASTE

## south team
Operations Team | SR Sub Type | Bill to Account Name | Site Account Name | SR Number | Billable Flag | SR Status | Sub Status | Sub Status Category | Quoted NTE Amount | WIP Labor | WIP Material | WIP Subcontractor | WIP Other | Total WIP | WIP Category | SR Description | Warranty Comment Date | Warranty Last Comment
260 Delmarva South Team SVC | Custom Quote | CBRE | BB&T 152379 | 1-47274943883 | Y | Open | Unscheduled | Branch Status | 4851.8 | 0 | 234 | 0 | 0 | 234 | Has WIP | CBRE BB &T Millington, MD 2 ton Heat Pump Replacement. Provide Labor only. Duct transitions to adapt to new unit. Misc. material copper fittings, insulations, brazing rod, nitrogen. Labor: $4172.32 Materials: $483.79 Total: $4656.11 This
260 Delmarva South Team SVC | Custom Quote | DELMAR SCHOOL DISTRICT | DELMAR SCHOOL DISTRICT | 1-47712376540 | Y | Scheduled | Tech Accepted | Branch Status | 2300 | 0 | 673.94 | 0 | 0 | 673.94 | Has WIP | Compressor replacement for classroom C127
260 Delmarva South Team SVC | Custom Quote | M & T BANK | MANUFACTURERS AND TRADERS TRUST COMPANY | 1-47721695016 | Y | Scheduled | Tech Accepted | Branch Status | 9588 | 0 | 3794.56 | 0 | 0 | 3794.56 | Has WIP | To provide all labor and materials to bring back Fan in fan house #6 to excellent condition per scope of work set forth by M&T Bank and site supervisor Joe Weiser
260 Delmarva South Team SVC | Custom Quote | STATE OF MARYLAND DEPT OF GEN SVCS | DEERS HEAD HOSPITAL CENTER | 1-47460471026 | Y | Open | Unscheduled | Branch Status | 3164.38 | 0 | 0 | 0 | 0 | 0 | No WIP | Eddy current testing chiller 1 All testing will need to scheduled time of maintenance 1 drain and remove condenser head 2 remove and drain evaporator head 3 test each tube for deficiencies in report condition 4 install heads replace and refill chiller n
260 Delmarva South Team SVC | Custom Quote | STATE OF MARYLAND DEPT OF GEN SVCS | DEERS HEAD HOSPITAL CENTER | 1-47461723583 | Y | Open | Unscheduled | Branch Status | 3164.38 | 0 | 0 | 0 | 0 | 0 | No WIP | Eddy current testing chiller 1 All testing will need to scheduled time of maintenance 1 drain and remove condenser head 2 remove and drain evaporator head 3 test each tube for deficiencies in report condition 4 install heads place system back in normal
260 Delmarva South Team SVC | Labor & Material |  | STATE OF DELAWARE | 1-47725102871 | Y | Scheduled | Tech Accepted | Branch Status |  | 763.73 | 0 | 0 | 147.6 | 911.33 | Has WIP | One (1) JOHNSON CONTROLS METASYS Direct Digital Control System Furnish and install a JOHNSON CONTROLS METASYS Building Automation System to control the following material list per plans:: QTY DESCRIPTION 1 Air Cooled Chiller (existing controller)
260 Delmarva South Team SVC | Labor & Material | BEEBE MEDICAL CENTER | BEEBE MEDICAL CENTER AUXILIARY, INC. | 1-47444970086 | Y | Audit | Invoice Pending | BRC Status |  | 683.35 | 0 | 0 | 45 | 728.35 | Has WIP | installing vgd valve on chiller 3 working on lean on chiller 1 looking at calibration on. Liquid level system 2
260 Delmarva South Team SVC | Labor & Material | CHESAPEAKE REHABILITATION | REHABILITATION HOSPITAL CORPORATION OF AMERICA | 1-46753378919 | Y | Open | Unscheduled | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Clean Boiler
260 Delmarva South Team SVC | Labor & Material | COUNTRY SCHOOL | THE COUNTRY SCHOOL INC | 1-46567755694 | Y | Scheduled | Tech Accepted | Branch Status |  | 339.44 | 0 | 0 | 27 | 366.44 | Has WIP | Zone 6 pump 6 not running
260 Delmarva South Team SVC | Labor & Material | HARRISON GROUP | HARRISON SUITES HOTEL | 1-47308623255 | Y | Scheduled | Tech Accepted | Branch Status |  | 0 | 235.96 | 0 | 0 | 235.96 | Has WIP | Replace leaving water temp sensor and discharge sensor
260 Delmarva South Team SVC | Labor & Material | MEBA | THE CALHOON M E B A ENGINEERING SCHOOL ALUMNI ASSOCIATION INC | 1-46763501372 | Y | Scheduled | Tech Accepted | Branch Status |  | 554.87 | 0 | 0 | 23.4 | 578.27 | Has WIP | Provide customer with six well mounted 8" temperature sensors and six stainless steel thermowells for their installation into predetermined pipe locations. Also provide an FEC controller, to be customer installed, for connection of sensors. Customer to pr
260 Delmarva South Team SVC | Labor & Material | TALBOT COUNTY COURT HOUSE | COUNTY OF TALBOT | 1-45472099250 | Y | Open | Unscheduled | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Heat pumps not working
260 Delmarva South Team SVC | Labor & Material | TALBOT COUNTY COURT HOUSE | COUNTY OF TALBOT | 1-45875670573 | Y | Open | Unscheduled | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Check controls for boilers
260 Delmarva South Team SVC | Labor & Material | TALBOT CTY BD OF EDUCATION | TALBOT COUNTY PUBLIC SCHOOLS | 1-47163072769 | Y | Open | Unscheduled | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Check control for fuel pumps
260 Delmarva South Team SVC | Labor & Material | TALBOT CTY BD OF EDUCATION | TALBOT COUNTY PUBLIC SCHOOLS | 1-47905415694 | Y | Scheduled | Tech Accepted | Branch Status |  | 169.72 | 0 | 0 | 22.5 | 192.22 | Has WIP | MOTON ELEMENTARY SCHOOL Pneumatic controls issues
260 Delmarva South Team SVC | Labor & Material | UNIVERSITY OF MARYLAND | UMES-KIAH HALL | 1-47978223275 | Y | Scheduled | Tech Accepted | Branch Status |  | 763.73 | 0 | 0 | 99 | 862.73 | Has WIP | Repairs due to flooding
260 Delmarva South Team SVC | Labor & Material | UNIVERSITY OF MARYLAND MEDICAL SYSTEM | DORCHESTER GENERAL HOSPITAL INC | 1-47238917340 | Y | Open | Unscheduled | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | CANCER CENTER Replace DP sensor for AHU #1
260 Delmarva South Team SVC | Labor & Material | UNIVERSITY OF MARYLAND MEDICAL SYSTEM | MEMORIAL HOSPITAL OF EASTON, MD INC | 1-45928602652 | Y | In Progress | Unscheduled | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Materials for static pressure sensor on air handler performed on 1/17/17.
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | 1-46715980813 | Y | Open | Unscheduled | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | 1-46715981004 | Y | Open | Unscheduled | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | 1-46715981195 | Y | Open | Unscheduled | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | 1-46715981386 | Y | Open | Unscheduled | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | 1-46715981627 | Y | Open | Unscheduled | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | 1-46716230828 | Y | Open | Unscheduled | Branch Status | 349 | 0 | 0 | 0 | 0 | 0 | No WIP | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | DART FEDERALSBURG MD | 1-41337839761 | Y | Open | Unscheduled | Branch Status | 4480 | 0 | 0 | 0 | 0 | 0 | No WIP | DX Indoor Scroll Chiller w/Remote Cond. - CH-1¦Start up/PCAT - Branch: Baltimore MD Service - 0319 in 2016
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | LAUREL ES | 1-46419593673 | Y | Open | Unscheduled | Branch Status | 512 | 0 | 0 | 0 | 0 | 0 | No WIP | YVAA - Air Cooled Chiller - CH-2FINAL¦Connectivity - Connectivity - BACnet, Commissioning Labor, Installation Year: 2016
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | LAUREL ES | 1-46420525302 | Y | Open | Unscheduled | Branch Status | 1280 | 0 | 0 | 0 | 0 | 0 | No WIP | YVAA - Air Cooled Chiller - CH-2FINAL¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2016
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | LAUREL ES | 1-46711537214 | Y | Open | Unscheduled | Branch Status | 512 | 0 | 0 | 0 | 0 | 0 | No WIP | YLAA - Air Cooled Scroll Chiller - CH-1FINAL¦Connectivity - Connectivity - BACnet, Commissioning Labor, Installation Year: 2016
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | LAUREL ES | 1-46711602113 | Y | Open | Unscheduled | Branch Status | 1280 | 0 | 0 | 0 | 0 | 0 | No WIP | YLAA - Air Cooled Scroll Chiller - CH-1FINAL¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2016
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | LOVE CREEK ELEMENTARY SCHOOL | 1-37220863153 | Y | Open | Unscheduled | Branch Status | 1280 | 0 | 0 | 0 | 0 | 0 | No WIP | YVAA - Air Cooled Chiller - CH-1¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2016
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | SALISBURY UNIVERSITY CHILLER #2 | 1-46545248534 | Y | Scheduled | Tech Accepted | Branch Status | 1980 | 1310.41 | 0 | 0 | 94 | 1404.41 | Has WIP | YVWA - Water Cooled Chiller - CH-2¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2017
260 Delmarva South Team SVC | PCAT Quoted | JCI US HVAC ES COMM SERV | SALISBURY UNIVERSITY CHILLER #2 | 1-46912723987 | Y | Open | Unscheduled | Branch Status | 4000 | 0 | 0 | 0 | 0 | 0 | No WIP | YVWA - Water Cooled Chiller - CH-2¦Field Labor (except PCAT) - 2 Yr Startup/Shutdown
260 Delmarva South Team SVC | ROC Applications | M&E SALES | SALISBURY MIDDLE SCHOOL | 1-46692787779 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Late to Test ROC alarm / Acc. # 6160-4649-653349/ / SET00108D04A94B Timestamp 02/12/2017 08:07:00 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
260 Delmarva South Team SVC | ROC Applications | SALISBURY UNIVERSITY | SALISBURY UNIVERSITY | 1-47317062346 | Y | Open | Priority Dispatch AM | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | Operating Alarm ROC alarm / Acc. # 6807-7593-669440/ 650/ SBCM166789 To place a disregard for this or any other signal, call the ROC at 800-753-4524 Opt. 1 and supply the operator with the Acct Number listed above 02/23/2017 21:16:25 CH-1 SYS 1 FAULT
260 Delmarva South Team SVC | ROC Applications | SALISBURY UNIVERSITY | SALISBURY UNIVERSITY | 1-47920356064 | Y | Scheduled | Tech Accepted | Branch Status |  | 341.67 | 0 | 0 | 18 | 359.67 | Has WIP | Operating Alarm ROC alarm / Acc. # 6807-7676-687421/ 650/ SBCM166789 To place a disregard for this or any other signal, call the ROC at 800-753-4524 Opt. 1 and supply the operator with the Acct Number listed above 03/07/2017 18:56:33 CH-1 SYS 1 FAULT
260 Delmarva South Team SVC | Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | BEEBE MEDICAL CENTER AUXILIARY, INC. | 1-47920268136 | N | Open | Unscheduled | Branch Status |  | 0 | 0 | 0 | 0 | 0 | No WIP | To invoice at cost for 2,935 pounds of R-134a for Beebe Medical Center
260 Delmarva South Team SVC | Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | DISCOVER FINANCIAL SERVICES | 1-46705065041 | N | Scheduled | Tech Accepted | Branch Status |  | 472.47 | 0 | 0 | -472.47 | 0 | No WIP | project 7N28-0017
260 Delmarva South Team SVC | Shared Resource to Projects | JCI US SS INTERCOMPANY SUBCONTRACT | LOWER EASTERN SHORE CHILDRENS CENTER | 1-46577469154 | N | Scheduled | Tech Accepted | Branch Status |  | 7406.79 | 323.88 | 0 | -7730.67 | 0 | No WIP | Project #5N270298
260 Delmarva South Team SVC | Warranty to Equipment | OHIO CAT | OHIO CAT | 1-47867047924 | N | Scheduled | Scheduled After Hours | Branch Status |  | 684.51 | 2776 | 0 | -3460.51 | 0 | No WIP | Loc: Perdue, 6906 Zion Church Rd, Salisbury, MD 21804 Due: 3/6/17 Emg Desc: 100 ton rental chiller shut down on motor pressure high pressure cut out and low suction pressure Update 6am : Compressor was found to have blown up and needs to be repl | 2017-03-06 | Extended Warranties on Claim :

## Open SR Report - N28 - All Team
Snapshot Date | Region | Sub-Region | Branch Number | Branch | Operations Team | Branch Category | SR Number | ROW_ID | LOB | SR Type | SR Sub Type | SR Category | Bill to Account Name | Site Account Name | Billable Flag | Opened Date | Days Open | Days Open Bucket1 | Days Open Bucket2 | Labor Hours | SR Status | Sub Status | Sub Status Category | Status Last Updated | Days In Sub Status | Days In Sub Status Bucket | Quoted NTE Amount | WIP Labor | WIP Material | WIP Subcontractor | WIP Other | Total WIP | WIP Category | Last Labor Date | Days Since Last Labor | Last Labor Bucket1 | Last Labor Bucket2 | Has Claim | SD Claim # | Warranty SubType | Warranty Bucket1 | Claim Status | Claim Date | Claim Days Open | Claim Error Date | Claim Error Description | Branch Action | Employee Login | Days Open Bucket 3 | SR Description | Warranty Comment Date | Warranty Last Comment
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-28106927932 | 1-CWU50E4 | HVAC-Equipment | L&M | Condition A | Non-Quoted | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | Y | 2015-12-31 15:35 | 435 | > 120 | > 120 |  | Completed | Customer Accepted | Branch Status | 2016-10-27 12:37 | 134 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | > 120 | Condition A
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-28106928104 | 1-CWU50IW | HVAC-Equipment | L&M | Condition A | Non-Quoted | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | Y | 2015-12-31 15:35 | 435 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2015-12-31 15:35 | 435 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | > 120 | Condition A
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45920666164 | 1-L3FZ8S4 | HVAC-Equipment | L&M | Custom Quote | Quoted | ASHLAND INC | ASHLAND BUILDING 8100 | Y | 2017-01-26 21:17 | 43 | 31 to 60 | 41 to 50 | 18 | Scheduled | Tech On Site | Branch Status | 2017-01-26 21:18 | 43 | 31 to 60 | 5451 | 1935.76 | 0 | 1266 | 36 | 3237.76 | Has WIP | 2017-03-08 | 2 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | Building 8100 Trane CVHF770 s/n L98C01705 Perform eddycurrent testing on all condenser and evaporator tubes. Lock out / tag out unit. Isolate and drain condenser and evaporator bundles. Remove condenser and evaporator heads. Brush clean all evaporat
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45920666670 | 1-L3FZ966 | HVAC-Equipment | L&M | Custom Quote | Quoted | ASHLAND INC | ASHLAND BUILDING 8136A | Y | 2017-01-26 21:19 | 43 | 31 to 60 | 41 to 50 | 27 | Scheduled | Tech Accepted | Branch Status | 2017-01-26 21:20 | 43 | 31 to 60 | 5928 | 2391.95 | 118.89 | 1565 | 67.5 | 4143.34 | Has WIP | 2017-03-07 | 3 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | Building 8136A York m/n YTK7D6F1-CSH s/n GLGM046754 Perform eddycurrent testing on all condenser and evaporator tubes. Lock out / tag out unit. Isolate and drain condenser and evaporator bundles. Remove condenser and evaporator heads. Brush clean al
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46898395673 | 1-LJM3DP5 | HVAC-Equipment | L&M | Custom Quote | Quoted | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | Y | 2017-02-15 17:20 | 23 | 1 to 30 | 21 to 30 |  | Scheduled | Pending Arrival | Branch Status | 2017-02-15 17:22 | 23 | 15 to 30 | 8358 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | BLDG #200 Chiller #1 and #2 Eddycurrent Testing York Model #YKDCDRQ4-CJGS Lock out/tag out chiller. Isolate and drain down condenser and evaporator bundles Store glycol form evaporator into drums. Remove heads and mechanically brush clean all tub
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47714992937 | 1-LX49W6H | HVAC-Equipment | L&M | Custom Quote | Quoted | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | Y | 2017-03-01 16:25 | 9 | 1 to 30 | 7 to 13 | 0 | Scheduled | Tech Accepted | Branch Status | 2017-03-01 16:26 | 9 | 8 to 14 | 1723.4 | 0 | 67.21 | 0 | 0 | 67.21 | Has WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | DuPont Stine BLDG 190 New Chiller Mount and add temperature controller to unit enable circuit. Wire and test operation of new control
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47863208363 | 1-LZKINXN | HVAC-Equipment | L&M | Custom Quote | Quoted | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | Y | 2017-03-05 16:24 | 5 | 1 to 30 | 4 to 6 | 0 | Scheduled | Tech Accepted | Branch Status | 2017-03-05 16:25 | 5 | 3 to 7 | 2653.99 | 0 | 157.35 | 0 | 0 | 157.35 | Has WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | DuPont Stine BLDG 215 Chiller #1 Replace Failed Oil Cooler TXV valve. Lock out tag out chiller. Isolate valve and remove TXV. Install new TXV with access port. Pull vacuum on line. Open valves and check for leaks. Start up chiller and check operat
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47910259143 | 1-M0CJ4JR | HVAC-Equipment | L&M | Custom Quote | Quoted | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | Y | 2017-03-07 17:48 | 3 | 1 to 30 | 1 to 3 | 4 | Scheduled | Tech Accepted | Branch Status | 2017-03-07 17:49 | 3 | 3 to 7 | 11202.76 | 429.62 | 1760.68 | 0 | 9 | 2199.3 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | DuPont Stine BLDG 120 System #1 MO-99 Refrigerant Chiller Leak Repairs. Lock out tag out chiller. Repair leaking copper suction line by relief valves. Replace leaking compressor motor terminals. Replace leaking oil cooler sight glass. Pressurize sy
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-35209755059 | 1-G6AZ8VN | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT | DUPONT CHESTNUT RUN | Y | 2016-06-17 17:15 | 266 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-06-17 17:15 | 266 | > 120 | 2920.85 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | > 120 | York chiller model ylaa0115 serial 2gym017106. Remove leaving chilled water sensor and replace with new. Part # 025-29964-000f. Check operation of new sensor. System 2 recover remaining r410a , and pressure test with nitrogen. Evacuate and charge with
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-37481561411 | 1-H7VJXVN | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT | DUPONT CHESTNUT RUN | Y | 2016-08-24 22:17 | 198 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-08-24 22:17 | 198 | > 120 | 9481 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Building #713 Chiller m/n YLAA0115SE46XCADBTCAX s/n 2GYM017106 Furnish and replace qty-1 leaking condenser coil on circuit #2. Lock out / tag out all energy sources. Recover and dispose of old refrigerant charge. Disconnect piping and remove old coi
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-37495128439 | 1-H83MQ9J | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT | DUPONT CHESTNUT RUN | Y | 2016-08-25 13:09 | 197 | > 120 | > 120 | 0 | Pending Adjustment | Pending Adjustment | Branch Status | 2016-10-03 16:29 | 158 | > 120 | 2959 | 0 | 0 | 0 | 0 | 0 | No WIP | 2016-08-31 | 191 | > 120 | > 120 | No | [9 empty] | CDOLPHL | > 120 | Troubleshoot VFD Fault. Ycaa0275/ 2dym015748 Remove and replace bleed down resistors on chiller 1 drive that are causing trouble faults on dc bus. Test drive operation. Labor 18 hrs @ $146.72 Parts. $318.00
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-36028109391 | 1-GJU7F4F | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2016-07-08 18:33 | 245 | > 120 | > 120 | 0 | Pending Adjustment | Pending Adjustment | Branch Status | 2016-08-30 10:49 | 192 | > 120 | 2099.2 | 0 | 0 | 0 | 0 | 0 | No WIP | 2016-07-21 | 232 | > 120 | > 120 | No | [9 empty] | CDOLPHL | > 120 | ABSORBER #2 FURNISH 18 New PALL Bromide Solution FILTERS to REPLENISH Supply onsite. (6 Filters per Changeout) REMOVE and REPLACE current clogged Filters CLEAN out Canister EVACUATE and RETURN to Service
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46438155392 | 1-LC02U0W | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-02-01 20:21 | 37 | 31 to 60 | 30 to 40 | 8 | Scheduled | Tech Accepted | Branch Status | 2017-02-01 20:21 | 37 | 31 to 60 | 4112.16 | 728.16 | 0 | 0 | 45 | 773.16 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | CHILLER #10 EDDY-CURRENT EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR & CONDENSER TUBES (1,582 TOTAL) FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED UPON COMPLETION. *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED AND BRUSHED BEFORE TECHNICIAN ARRIV
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46718363513 | 1-LGMWNZT | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-02-13 20:55 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 20:55 | 25 | 15 to 30 | 8699.09 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4.975ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: TR
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46719052659 | 1-LGNBFQR | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-02-13 20:45 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 20:45 | 25 | 15 to 30 | 8699.09 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4.975ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: TR
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47436369564 | 1-LSIE10C | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-02-28 15:22 | 10 | 1 to 30 | 7 to 13 | 6 | Scheduled | Tech Accepted | Branch Status | 2017-02-28 15:22 | 10 | 8 to 14 | 988 | 546.13 | 0 | 0 | 13.5 | 559.63 | Has WIP | 2017-02-28 | 10 | 1 to 30 | 7 to 13 | No | [9 empty] | CDOLPHL | 1 to 90 | (6501697258) CHILLER #9 EVAPORATOR WATERBOX REPAIRS: CLEAN AND PREPARE TUBE SHEET DIVISION PLATE TRACKING FOR STEEL EPOXY COATING APPLY BELZONA 1121 "SUPER XL-METAL" (PURCHASED UNDER DUPONT PO#: 6501690015) TO FILL IN PITS AND GOUGING CLEAN UP AND
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47443336030 | 1-LSMJCDA | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-02-28 17:52 | 10 | 1 to 30 | 7 to 13 | 33 | Scheduled | Tech Accepted | Branch Status | 2017-02-28 17:54 | 10 | 8 to 14 | 4740.1 | 3003.69 | 93.67 | 0 | 126 | 3223.36 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | (6501709952) Chiller #10 Annual Maintenance 2017 Remove Refrigerant Sample for Chemical Analysis Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filt
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47873229676 | 1-LZQHGFG | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-03-06 12:48 | 4 | 1 to 30 | 4 to 6 | 4 | Scheduled | Tech On Site | Branch Status | 2017-03-06 12:49 | 4 | 3 to 7 | 1296.26 | 364.08 | 8.3 | 0 | 18 | 390.38 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | (6501711947) CHILLER #10: Due to Refrigerant Leaks discovered on 03/03/2017 the following work is Recommended: Transfer entire R-134A charge to YORK Central Recovery Tank. Document weight of charge and calculated percentage loss based on design. P
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47874641859 | 1-LZRBQ2R | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-03-06 12:55 | 4 | 1 to 30 | 4 to 6 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-06 12:57 | 4 | 3 to 7 | 1432.06 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | E306 RTP Chilled Water Loop: Calculate appropriate System Fill Pressure based on height of highest coil and specific gravity of the Chilled Water. Isolate/Drain Expansion Tank. Increase Expansion Tank Bladder Pressure to System Fill Pressure with Nitr
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47953222455 | 1-M123Z93 | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-03-08 20:05 | 2 | 1 to 30 | 1 to 3 | 6 | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:06 | 2 | 1 to 2 | 3950 | 546.12 | 0 | 0 | 38.34 | 584.46 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | CHILLER #10 REFRIGERANT PIPING LEAK REPAIR: REPAIR OF THE FOLLOWING LEAKS FOUND ON 03/03/17: 1-1/2" THREADED LIQUID REFRIGERANT TEE FEEDING OIL COOLER COMP. OIL RESERVOIR EQUALIZING LINE 1/4 THREADED FLARE ELBOW CUT & DISMANTLE REFRIGERANT
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47954372704 | 1-M12SMSG | HVAC-Equipment | L&M | Custom Quote | Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-03-08 20:16 | 2 | 1 to 30 | 1 to 3 | 2 | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:17 | 2 | 1 to 2 | 2601.37 | 182.04 | 1017.62 | 0 | 13.5 | 1213.16 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | CHILLER #10 PRV SHAFT SEAL REPLACEMENT REPAIR OF THE FOLLOWING REFRIGERANT LEAK FOUND ON 03/03/17: COMPRESSOR PRE-ROTATION VANE SHAFT SEAL DISSMANTLE & REMOVE OLD SEAL ASSEMBLY FURNISH & INSTALL NEW SEAL ASSEMBLY WITH NEW ORINGS, GASKET, & FASTE
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-36622889549 | 1-GTOBMFH | HVAC-Equipment | L&M | Custom Quote | Quoted | EAST COAST PLUMBING & HVAC INC | COUNCIL OF THE DEVON | Y | 2016-07-28 18:46 | 225 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-07-28 18:46 | 225 | > 120 | 57689 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Repairs to York YT Chiller m/n YTG3A3B2-CGHS s/n GMLM143031 Mobilize all tools and equipment. Lock out / tag out unit. Recover, weigh, and store entire refrigerant charge. Disconnect motor wiring and compressor coupling. Set up rigging and remove com
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-36630502193 | 1-GTSUSDT | HVAC-Equipment | L&M | Custom Quote | Quoted | EAST COAST PLUMBING & HVAC INC | COUNCIL OF THE DEVON | Y | 2016-07-28 21:09 | 225 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-07-28 21:09 | 225 | > 120 | 57689 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Repairs to York YT Chiller m/n YTG3A3B2-CGHS s/n GMLM143031 Mobilize all tools and equipment. Lock out / tag out unit. Recover, weigh, and store entire refrigerant charge. Disconnect motor wiring and compressor coupling. Set up rigging and remove com
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-42618642157 | 1-JKU1ER1 | HVAC-Equipment | L&M | Custom Quote | Quoted | HBS EAST SOUTH CENTRAL WEST | MCC OPS-1 - JPM | Y | 2016-11-23 16:47 | 107 | 91 to 120 | 101 to 110 | 1 | Scheduled | Tech Accepted | Branch Status | 2016-11-23 16:47 | 107 | 91 to 120 | 5536 | 108.52 | 11.84 | 0 | 7.2 | 127.56 | Has WIP | 2016-12-30 | 70 | 61 to 90 | 61 to 70 | No | [9 empty] | CDOLPHL | 90 to 120 | Program Optiview panel, connect wiring in Optiview panel in data center chillers DCCH1, DCCH2, DCCH3, DCCH4, test operation of reset temperature controls.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47948959072 | 1-M0ZKLLS | HVAC-Equipment | L&M | Custom Quote | Quoted | ID GRIFFITH | I D GRIFFITH INC - WILMINGTON | Y | 2017-03-08 18:36 | 2 | 1 to 30 | 1 to 3 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-08 18:37 | 2 | 1 to 2 | 9833 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | CDC-1 Bear, DE Provide qty-40 hrs of technician labor to test and commission RTU Power Exhaust systems and VFD's. Also provide qty-10 hrs labor on a Saturday to perfrom testing and verification.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-42983053543 | 1-JQV00DJ | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | CDC1 - JONES LANG LASALLE - JPM | Y | 2016-12-07 15:05 | 93 | 91 to 120 | 91 to 100 |  | Open | Unscheduled | Branch Status | 2016-12-07 15:05 | 93 | 91 to 120 | 500 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 90 to 120 | Customer Work Order #25837981-1 RTU-3 Sensor Fail Alarm Checked sensor failure problem on unit RTU-3. Found unit was configured for 4 stages of cooling and unit has only one stage. Configured unit properly. Unit stayed in dehumidification mode.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-29332670721 | 1-DH3WXKX | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | Y | 2016-02-16 00:15 | 388 | > 120 | > 120 | 0 | Pending Adjustment | Pending Adjustment | Branch Status | 2016-08-26 14:05 | 196 | > 120 | 11904.78 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDICKSM2 | > 120 | JCI provided Training to CDC2. Course 2102
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-43296624880 | 1-JW1OXKG | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | Y | 2016-12-19 16:58 | 81 | 61 to 90 | 81 to 90 | 0 | Pending Adjustment | Pending Adjustment | Branch Status | 2016-12-28 18:53 | 72 | 61 to 90 | 8626.8 | 0 | 0 | 0 | 0 | 0 | No WIP | 2016-12-25 | 75 | 61 to 90 | 71 to 80 | No | [9 empty] | CDOLPHL | 1 to 90 | CDC-2 Chiller 1B Leaking Oil Sight Glass Repair. (JPMC WO 27497175-1/ REQUEST ID 5271383) Lock out tag out chiller. Recover refrigerant charge. Remove oil and dispose off. Replace leaking oil sight glass and "O" rings. Install new sight glass and "
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46760131188 | 1-LHBRW50 | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | Y | 2017-02-14 16:07 | 24 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-14 16:07 | 24 | 15 to 30 | 10448.87 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | CDC-2 Chiller 2A Leaking Oil Sight Glass Repair and "O" ring replacement Lock out tag out chiller. Recover refrigerant charge. Remove oil and dispose of. Replace leaking oil sight glass and "O" rings. While charge is out of machine we will replace
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47273019847 | 1-LPT4VK7 | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | Y | 2017-02-22 17:12 | 16 | 1 to 30 | 14 to 20 |  | Scheduled | Tech Accepted | Branch Status | 2017-02-22 17:13 | 16 | 15 to 30 | 2103.57 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | (JLL PO 2274991) CDC-2 Chiller 1B VSD Fluid Replacement Lock out tag out vsd. Drain vsd fluid and remove all tubing. Install new tubing and fill with new drive fluid Labor = $147.00 @ 8 hrs. = $1,176.00 Material (3) VSD Fluid = $782.57 T
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47166975432 | 1-LO1ZZ60 | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | MCC - JPM | Y | 2017-02-17 20:21 | 21 | 1 to 30 | 21 to 30 | 20 | Scheduled | Tech Accepted | Branch Status | 2017-02-17 20:21 | 21 | 15 to 30 | 2763.4 | 1932.23 | 245 | 0 | 25.2 | 2202.43 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | (JLL PO 2156022) Johnson Controls Inc. will provide labor and material to perform the following; 1. Lockout tagout DCCT2 2. Drain oil into storage container. 3. Replace input shaft seal. 4. Reconnect coupling and align motor and gearbox with lazer a
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47167004638 | 1-LO20LPA | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | MCC - JPM | Y | 2017-02-17 20:25 | 21 | 1 to 30 | 21 to 30 | 16 | Audit | Invoice Pending | BRC Status | 2017-03-09 14:53 | 1 | 1 to 2 | 3987 | 1480.8 | 184.89 | 0 | 25.2 | 1690.89 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | (JLL PO 2156022) Johnson Controls Inc. will supply labor and material to perform the following DCCT4 REPLACE COUPLER ON MOTOR; 1. Lockout tagout cooling tower. 2. Remove old coupler connecting motor and gearbox. 3. Install new coupler. 4. Align motor
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47885260543 | 1-LZXNBI7 | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | MCC - JPM | Y | 2017-03-06 18:06 | 4 | 1 to 30 | 4 to 6 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-06 18:06 | 4 | 3 to 7 | 11386 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | (JLL PO 2287094) MCC OPS-3 Cooling Tower. Ceramic Cooling Tower Co. M/n C1130 Install qty-1 customer furnished tower gearbox. Install qty-1 customer furnished tower fan motor. Lock out / tag out all energy sources. Disassemble tower gearbox coupl
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47942847625 | 1-M0VXLZD | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | MCC - JPM | Y | 2017-03-08 16:02 | 2 | 1 to 30 | 1 to 3 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-08 16:02 | 2 | 1 to 2 | 395.85 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | (JLL WO28491742-1) Materials Only. Furnish qty-1 new PX110 Coupling insert for OPS Tower #2. Freight included. Pricing per JLL / JCI Contract Materials: qty-1 coupling insert $319.39 Overnight Freight $76.46 Total: $395.85
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47324367334 | 1-LQNPFJA | HVAC-Equipment | L&M | Custom Quote | Quoted | JONES LANG LASALLE AMERICAS INC | MCC OPS-1 - JPM | Y | 2017-02-24 12:54 | 14 | 1 to 30 | 14 to 20 |  | Scheduled | Tech Accepted | Branch Status | 2017-02-24 12:56 | 14 | 8 to 14 | 25123.79 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | (2276599) Clean cooling towers for OPSCT1, OPSCT2, and OPSCT3. Provide Vacuum Truck service and labor to clean the OPS Cooling Towers. Pricing per JLL / JCI agreement.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-43411666964 | 1-JXY6OLW | HVAC-Equipment | L&M | Custom Quote | Quoted | NORTHEAST UTILITIES SYSTEMS | DELAWARE SOLID WASTE AUTHORITY | Y | 2016-12-22 18:28 | 78 | 61 to 90 | 71 to 80 |  | Open | Unscheduled | Branch Status | 2016-12-22 18:28 | 78 | 61 to 90 | 3235 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | York m/n YCAL0074EB46X s/n RHPM012366 Recover / reclaim current 407c refrigerant charge from circuit 2. Remove leaking relief valve on discharge line. Furnish and nstall QTY-1 discharge relief valve on circuit 2 discharge line. Pressure test syst
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-34182431774 | 1-FPBC55Q | HVAC-Equipment | L&M | Custom Quote | Quoted | PROCTER & GAMBLE | PROCTOR & GAMBLE | Y | 2016-05-20 15:41 | 294 | > 120 | > 120 |  | Approved (Internal) | Approved (Internal) | Branch Status | 2016-05-20 15:46 | 294 | > 120 | 2450 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Provide HVAC service on a T&M basis 5-10-16.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47885111808 | 1-LZXK4QO | HVAC-Equipment | L&M | Custom Quote | Quoted | PROCTER & GAMBLE | PROCTOR & GAMBLE | Y | 2017-03-06 18:01 | 4 | 1 to 30 | 4 to 6 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-06 18:04 | 4 | 3 to 7 | 7782 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Chiller "B" m/n YTC3P3B2-CJD s/n YATM453436 Furnish and install qty-1 new carbon burting disk to replace defective Vent Guard Assembly. Lock out / tag out chiller. Recover, store, and weigh entire refrigerant charge. Disassemble old Vent Guard as
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47885260814 | 1-LZXNBPQ | HVAC-Equipment | L&M | Custom Quote | Quoted | PROCTER & GAMBLE | PROCTOR & GAMBLE | Y | 2017-03-06 18:13 | 4 | 1 to 30 | 4 to 6 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-06 18:16 | 4 | 3 to 7 | 9255 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | P&G Cooling Tower #5 Install customer supplied bearings on cooling tower. Lock out / tag out tower. Furnish install plywood across tower fill to prevent damage. Remove belts and fan pulley. Remove fan blade assembly. Remove shaft and bearings and
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47407296650 | 1-LS12W7E | HVAC-Equipment | L&M | Custom Quote | Quoted | ZACROS AMERICA INC | HEDWIN CORPORATION - NEWARK DE | Y | 2017-02-27 18:36 | 11 | 1 to 30 | 7 to 13 |  | Open | Unscheduled | Branch Status | 2017-02-27 18:36 | 11 | 8 to 14 | 1421 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | RTU #23 Carrier m/n 48TME008-A-601 s/n 0405G30410 Repair leak on discharge line of compressr. Reclaim and remove refrigerant from circuit #2. Pressure test system. Evacuate and perform a vacuum hold test. Recharge system with reclaimed refrigerant an
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-36321261099 | 1-GOOQOFF | HVAC-Equipment | L&M | Customer Care | Cost Write-Off | ASHLAND INC | ASHLAND INCORPORATED | N | 2016-07-19 14:50 | 234 | > 120 | > 120 | 35 | In Progress | Submitted | Branch Status | 2016-09-29 17:50 | 162 | > 120 |  | 2493.95 | -296.02 | 0 | 117 | 2314.93 | Has WIP | 2017-03-06 | 4 | 1 to 30 | 4 to 6 | No | [9 empty] | CDOLPHL | > 120 | Bldg. 8159 UPG WARRANTY-CLAIM #J382294 faulty compressor-ordering replacement compressor per John Walker s/n N1A6250678 J399804-2ND COMPRESSOR - claim not filed yet. need SI# and claim being built to deny due to 2 faulty claims back to back. working
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-35456691111 | 1-GADZXYF | HVAC-Equipment | L&M | Customer Satisfaction | Cost Write-Off |  | HOWARD R. YOUNG CORRECTIONAL INSTITUTION | N | 2016-06-25 12:04 | 258 | > 120 | > 120 |  | Scheduled | Pending Tech Acceptance | Branch Status | 2016-06-25 12:07 | 258 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Howard Young - Chiller - Failed suction pressure transducer for circuit 1 & 2 Problem: Failure on Circuit 1 and 2 Cause: Failed suction pressure transducer Resolution: Replace pressure transducer
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46753611814 | 1-LH7W5RA | HVAC-Equipment | L&M | Customer Satisfaction | Cost Write-Off | BANK OF AMERICA PAYMENT PREP GROUP | BOA DE5-001 | N | 2017-02-14 13:10 | 24 | 1 to 30 | 21 to 30 | 5 | In Progress | Review for Completion | Branch Status | 2017-02-16 19:44 | 22 | 15 to 30 |  | 559.34 | 0 | 0 | 14.4 | 573.74 | Has WIP | 2017-02-14 | 24 | 1 to 30 | 21 to 30 | No | [9 empty] | CDOLPHL | 1 to 90 | HOLDING SPOT FOR PM'S UNTIL SDP IS BUILT
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46710593901 | 1-LGIA4X9 | HVAC-Equipment | L&M | Customer Satisfaction | Cost Write-Off | BANK OF AMERICA PAYMENT PREP GROUP | BOA DE5-002 | N | 2017-02-13 17:05 | 25 | 1 to 30 | 21 to 30 | 5.5 | In Progress | Review for Completion | Branch Status | 2017-02-14 15:07 | 24 | 15 to 30 |  | 615.27 | 0 | 0 | 16.2 | 631.47 | Has WIP | 2017-02-13 | 25 | 1 to 30 | 21 to 30 | No | [9 empty] | CDOLPHL | 1 to 90 | HOLDING SPOT FOR PM'S UNTIL SDP IS BUILT.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46711908680 | 1-LGJ2BEW | HVAC-Equipment | L&M | Customer Satisfaction | Cost Write-Off | BANK OF AMERICA PAYMENT PREP GROUP | BOA DE5-003 | N | 2017-02-13 17:08 | 25 | 1 to 30 | 21 to 30 | 5.5 | Scheduled | Tech Accepted | Branch Status | 2017-02-13 17:10 | 25 | 15 to 30 |  | 615.27 | 0 | 0 | 28.8 | 644.07 | Has WIP | 2017-02-14 | 24 | 1 to 30 | 21 to 30 | No | [9 empty] | CDOLPHL | 1 to 90 | HOLDING SPOT FOR PM'S UNTIL SDP IS BUILT
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45901727510 | 1-L34PBME | HVAC-Equipment | L&M | Customer Satisfaction | Cost Write-Off | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | N | 2017-01-26 14:42 | 43 | 31 to 60 | 41 to 50 | 4 | In Progress | Returning For Completion | Branch Status | 2017-01-30 13:44 | 39 | 31 to 60 |  | 447.48 | 0 | 0 | 18 | 465.48 | Has WIP | 2017-02-21 | 17 | 1 to 30 | 14 to 20 | No | [9 empty] | CDOLPHL | 1 to 90 | (PSA) Both Chillers in alarm. Oil VFD and Transducer fault.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47294836691 | 1-LQ64HJN | HVAC-Equipment | L&M | Customer Satisfaction | Cost Write-Off | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | N | 2017-02-23 12:49 | 15 | 1 to 30 | 14 to 20 | 3 | Scheduled | Tech Accepted | Branch Status | 2017-02-23 12:50 | 15 | 15 to 30 |  | 335.6 | 0 | 0 | 11 | 346.6 | Has WIP | 2017-02-23 | 15 | 1 to 30 | 14 to 20 | No | [9 empty] | CDOLPHL | 1 to 90 | Chiller #2 loss of current alarm.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46714096111 | 1-LGKD78V | HVAC-Equipment | L&M | Customer Satisfaction | Cost Write-Off | DELAWARE STATE UNIVERSITY | DELAWARE STATE UNIVERSIT | N | 2017-02-13 18:41 | 25 | 1 to 30 | 21 to 30 | 76 | Scheduled | Tech On Site | Branch Status | 2017-02-13 18:42 | 25 | 15 to 30 |  | 5824.4 | 122.32 | 0 | 333 | 6279.72 | Has WIP | 2017-02-24 | 14 | 1 to 30 | 14 to 20 | No | [9 empty] | CDOLPHL | 1 to 90 | Meeting and asset collection 2/13 (CK, JK) Asset collection 2/14 (CK, KEwing). Asset collection 2/17 (CK) Asset collection 2/20 (CK, KEwing, DAmes) Asset collection 2/21 (CK) Asset collection 2/22 (CK) Asset collection 2/24 (CK) 2/28 D. Naber- Beta
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-43713008400 | 1-K2XLH5C | HVAC-Equipment | L&M | Customer Satisfaction | Cost Write-Off | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | N | 2016-12-28 20:01 | 72 | 61 to 90 | 71 to 80 | 0 | Scheduled | Tech Accepted | Branch Status | 2016-12-28 20:01 | 72 | 61 to 90 |  | 0 | 0 | 0 | 0 | 0 | No WIP | 2017-01-17 | 52 | 31 to 60 | 51 to 60 | No | [9 empty] | CDOLPHL | 1 to 90 | RUPTURED DISC REPAIR - MOVING TO QUOTE 1-K2OOT6G WHEN RAUL GETS PO. Temporary holding spot for Mr. Kevin Fraze.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-43022929401 | 1-JRIQOS9 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | ASHLAND INC | ASHLAND BUILDING 8100 | Y | 2016-12-08 21:14 | 92 | 91 to 120 | 91 to 100 |  | Scheduled | Pending Tech Acceptance | Branch Status | 2016-12-08 21:15 | 92 | 91 to 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 90 to 120 | TRANE PURGE
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46540218339 | 1-LDOUEAR | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | BANK OF AMERICA PAYMENT PREP GROUP | BOA DE5-011 | Y | 2017-02-06 14:32 | 32 | 31 to 60 | 30 to 40 | 25 | In Progress | Review for Completion | Branch Status | 2017-02-07 14:41 | 31 | 31 to 60 |  | 2664.2 | 0 | 0 | 48.6 | 2712.8 | Has WIP | 2017-03-02 | 8 | 1 to 30 | 7 to 13 | No | [9 empty] | CDOLPHL | 1 to 90 | BOILER REPAIR
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-35733786885 | 1-GEYZ2F9 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | BAYHEALTH MEDICAL KENT CAMPUS | BAYHEALTH MEDICAL KENT CAMPUS | Y | 2016-06-29 14:12 | 254 | > 120 | > 120 |  | Approved (Internal) | Approved (Internal) | Branch Status | 2016-06-29 16:21 | 254 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | DO NOT BILL BAY HEALTH. THIS WAS FROM QUOTED JOB 1-35402627134. TRAILING COSTS WILL HAVE TO GO BACK.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46599898355 | 1-LEODJOZ | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | BRANDYWINE REALTY TRUST | 300 DELAWARE AVENUE | Y | 2017-02-08 14:02 | 30 | 1 to 30 | 21 to 30 | 2 | Scheduled | Pending Tech Acceptance | Branch Status | 2017-02-08 14:07 | 30 | 15 to 30 |  | 223.74 | 369.01 | 0 | 4.5 | 597.25 | Has WIP | 2017-02-09 | 29 | 1 to 30 | 21 to 30 | No | [9 empty] | CDOLPHL | 1 to 90 | (PSA) CHLLER#1 PUMP VSD
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-37555971521 | 1-H93UT35 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | CAPITAL SCHOOL DISTRICT | WILLIAM HENRY MIDDLE SCHOOL | Y | 2016-08-27 12:42 | 195 | > 120 | > 120 |  | Scheduled | Tech Accepted | Branch Status | 2016-08-27 12:44 | 195 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | HOLDING SPOT FOR POSSIBLE TRAILING COSTS FROM SR 1-37491979933. LOOKING FOR AIR BLEEDER OR AIR VENT 8/24 COBERHL ACTIVITY 1-H7NO8IH
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45474073199 | 1-KW237FZ | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | CBRE GWS LLC CSC | CSC NEWARK | Y | 2017-01-09 14:49 | 60 | 31 to 60 | 51 to 60 |  | Scheduled | Tech On Site | Branch Status | 2017-01-09 14:50 | 60 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Two stairwell electric unit heaters, wall mounted, not working (Norman Marks).
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47345766979 | 1-LR0G3LV | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | Y | 2017-02-25 00:47 | 13 | 1 to 30 | 7 to 13 | 9 | Scheduled | Scheduled After Hours | Branch Status | 2017-02-25 00:55 | 13 | 8 to 14 |  | 1289.65 | 780.29 | 0 | 40.5 | 2110.44 | Has WIP | 2017-03-07 | 3 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | Due: 24-Feb Desc: Chiller is down Svc Hrs: Right Now Access: Call site POC, need to fill out safety analysis Contact: Shawn 302-377-0771 Caller: Shawn 302-377-0771
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47459196361 | 1-LSVZAA1 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | Y | 2017-02-28 20:52 | 10 | 1 to 30 | 7 to 13 | 18 | Scheduled | Pending Tech Acceptance | Branch Status | 2017-02-28 20:55 | 10 | 8 to 14 |  | 2027.81 | 696.48 | 0 | 36 | 2760.29 | Has WIP | 2017-03-03 | 7 | 1 to 30 | 7 to 13 | No | [9 empty] | CDOLPHL | 1 to 90 | SYSTEM 1 LEAK CHECK BLDG 120
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47875218740 | 1-LZRO378 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | Y | 2017-03-06 13:17 | 4 | 1 to 30 | 4 to 6 | 10 | Scheduled | Tech Accepted | Branch Status | 2017-03-06 13:19 | 4 | 3 to 7 |  | 1121.31 | 154.57 | 0 | 9 | 1284.88 | Has WIP | 2017-03-07 | 3 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | Bldg 210N, Leak Check System 2
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47402231723 | 1-LRY2C2Z | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-02-27 16:57 | 11 | 1 to 30 | 7 to 13 | 1 | Scheduled | Tech Accepted | Branch Status | 2017-02-27 17:01 | 11 | 8 to 14 |  | 91.02 | 113.6 | 0 | 0 | 204.62 | Has WIP | 2017-02-27 | 11 | 1 to 30 | 7 to 13 | No | [9 empty] | CDOLPHL | 1 to 90 | (EMERG. PO 6501690015) Order Goodway Brushes fro tube cleaning.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47405246199 | 1-LRZUY2F | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-02-27 17:08 | 11 | 1 to 30 | 7 to 13 | 0 | Scheduled | Tech On Site | Branch Status | 2017-02-27 17:09 | 11 | 8 to 14 |  | 0 | 0 | 0 | 0 | 0 | No WIP | 2017-02-28 | 10 | 1 to 30 | 7 to 13 | No | [9 empty] | CDOLPHL | 1 to 90 | (temporary holding spot for #9 Waterbox repair under PO 6501697258- NEED QUOTE)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47444087633 | 1-LSMZGB5 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | E I DUPONT DENEMOURS CO | DUPONT EXPERIMENTAL STATION | Y | 2017-02-28 18:15 | 10 | 1 to 30 | 7 to 13 | 4 | Scheduled | Tech On Site | Branch Status | 2017-02-28 18:16 | 10 | 8 to 14 |  | 364.08 | 554 | 0 | 13.5 | 931.58 | Has WIP | 2017-02-28 | 10 | 1 to 30 | 7 to 13 | No | [9 empty] | CDOLPHL | 1 to 90 | Chiller #9 Condenser tube plugging.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47310176595 | 1-LQF99W3 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | EDGEWELL PERSONAL CARE BRANDS LLC | EDGEWELL PERSONAL CARE | Y | 2017-02-23 21:00 | 15 | 1 to 30 | 14 to 20 | 8 | Audit | Invoice Pending | BRC Status | 2017-03-03 19:11 | 7 | 3 to 7 |  | 894.94 | 0 | 0 | 68.8 | 963.74 | Has WIP | 2017-02-24 | 14 | 1 to 30 | 14 to 20 | No | [9 empty] | CDOLPHL | 1 to 90 | Chiller #3 running low line voltage.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47495273517 | 1-LTHGJL9 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | EDGEWELL PERSONAL CARE BRANDS LLC | EDGEWELL PERSONAL CARE | Y | 2017-03-01 00:15 | 9 | 1 to 30 | 7 to 13 | 0 | Scheduled | Pending Tech Acceptance | Branch Status | 2017-03-01 00:16 | 9 | 8 to 14 |  | 0 | 100.87 | 0 | 0 | 100.87 | Has WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | CONTINUATION OF CHILLER #3 RUNNING LOW LINE VOLTAGE (1-47310176595)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47873229521 | 1-LZQHGB5 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | EDGEWELL PERSONAL CARE BRANDS LLC | EDGEWELL PERSONAL CARE | Y | 2017-03-06 12:46 | 4 | 1 to 30 | 4 to 6 | 8 | Scheduled | Tech On Site | Branch Status | 2017-03-06 12:47 | 4 | 3 to 7 |  | 894.94 | 0 | 0 | 68.8 | 963.74 | Has WIP | 2017-03-06 | 4 | 1 to 30 | 4 to 6 | No | [9 empty] | CDOLPHL | 1 to 90 | Install customer supplied starter logic board on Chiller #3.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45064355272 | 1-KPA5J2G | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | JONES LANG LASALLE AMERICAS INC | CDC1 - JONES LANG LASALLE - JPM | Y | 2017-01-03 15:35 | 66 | 61 to 90 | 61 to 70 | 0 | Scheduled | Tech Accepted | Branch Status | 2017-01-03 15:38 | 66 | 61 to 90 |  | 0 | 0 | 0 | 0 | 0 | No WIP | 2017-01-06 | 63 | 61 to 90 | 61 to 70 | No | [9 empty] | CDOLPHL | 1 to 90 | JPMC REQUEST ID 5340049: WC 3A Oil filter leak on service valve.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45669372938 | 1-KZAD5OQ | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | Y | 2017-01-17 14:53 | 52 | 31 to 60 | 51 to 60 | 0 | Scheduled | Tech Accepted | Branch Status | 2017-01-17 14:56 | 52 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP | 2017-01-19 | 50 | 31 to 60 | 41 to 50 | No | [9 empty] | CDOLPHL | 1 to 90 | Chiller 3B experiencing Proof of Run Fault.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45677493703 | 1-KZF77PJ | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | Y | 2017-01-17 19:21 | 52 | 31 to 60 | 51 to 60 |  | Open | NSA Priority | Branch Status | 2017-01-17 19:30 | 52 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | JPMC Request ID: N/A Call Center Reference #: 27816852-1 NTE: $500 Due: 1/17/2017 Desc: Provide a tech to investigate a loss of proof of chiller running. Svc Hrs: N/A Access: N/A Contact: Jamie Powers Caller: Email
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46538281675 | 1-LDNOVYJ | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | Y | 2017-02-06 13:41 | 32 | 31 to 60 | 30 to 40 | 0 | Scheduled | Pending Tech Acceptance | Branch Status | 2017-02-06 13:42 | 32 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP | 2017-02-14 | 24 | 1 to 30 | 21 to 30 | No | [9 empty] | CDOLPHL | 1 to 90 | CHILLER 2A SIGHT GLASS REPAIR KEVIN PROVIDED QUOTE TO DAN LAZCO AWAITING PO/WO#
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45949176549 | 1-L3WYBJ9 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | JONES LANG LASALLE AMERICAS INC | MCC - JPM | Y | 2017-01-27 19:56 | 42 | 31 to 60 | 41 to 50 |  | Scheduled | Tech Accepted | Branch Status | 2017-01-27 19:58 | 42 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | EDDY CURRENT TESTING - COSTS NEED TO GO BACK TO SR 1-42867322672 THAT WAS BILLED ON 1/26.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45595519441 | 1-KY2E7YP | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | JONES LANG LASALLE AMERICAS INC | MCC OPS-1 - JPM | Y | 2017-01-13 13:06 | 56 | 31 to 60 | 51 to 60 | 0 | Scheduled | Tech Accepted | Branch Status | 2017-01-13 13:09 | 56 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP | 2017-01-27 | 42 | 31 to 60 | 41 to 50 | No | [9 empty] | CDOLPHL | 1 to 90 | WO: 27780679-1 JPMC REQ ID: 5390752 JCI TO INVESTIGATE OPERATIONS CENTER CHILLER 2 EXCESSIVE PURGE/ HIGH CONDENSING PRESSURE
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47812307187 | 1-LYQ7OC3 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | M DAVIS & SONS INC | JCI BATTERY DIVISION | Y | 2017-03-03 14:59 | 7 | 1 to 30 | 7 to 13 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-03 15:23 | 7 | 3 to 7 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Jeff Lidke (302) 893-8007 of M Davis stated while pulling wires for Chiller install, a wire came in contact with the board. Request to replace board and inspect board on second chiller.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47420983445 | 1-LS98905 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | NEWS JOURNAL COMPANY | WILMINGTON NEWS JOURNAL | Y | 2017-02-28 01:04 | 10 | 1 to 30 | 7 to 13 | 13 | Scheduled | Tech Accepted | Branch Status | 2017-02-28 01:05 | 10 | 8 to 14 |  | 1454.28 | 0 | 0 | 9.9 | 1464.18 | Has WIP | 2017-03-01 | 9 | 1 to 30 | 7 to 13 | No | [9 empty] | CDOLPHL | 1 to 90 | John Walker discussed issue with Craig M.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45596708966 | 1-KY33PT2 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | RESOLUTE INDUSTRIAL | RESOLUTE INDUSTRIAL - DE | Y | 2017-01-13 14:15 | 56 | 31 to 60 | 51 to 60 |  | Scheduled | Tech Accepted | Branch Status | 2017-01-13 14:16 | 56 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Overtime requested by customer. 01/13-14/2017
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47889534596 | 1-M006XDW | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE ALLEN LABS | Y | 2017-03-06 20:20 | 4 | 1 to 30 | 4 to 6 | 12 | Scheduled | Tech Accepted | Branch Status | 2017-03-06 20:22 | 4 | 3 to 7 |  | 1566.15 | 1197.5 | 0 | 18.9 | 2782.55 | Has WIP | 2017-03-08 | 2 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | Emergency Service call for York Chiller down to be performed under Work Order 469057.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47974511134 | 1-M1ES9PA | HVAC-Equipment | Material Only | Material Only Quote | Quoted | CBRE GWS LLC CSC | CSC NEWARK | Y | 2017-03-09 15:54 | 1 | 1 to 30 | 1 to 3 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-09 15:55 | 1 | 1 to 2 | 481.06 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | (WO C128923) Materials Only: Johnson Controls is to furnish qty-2 replacement fan motors for unit heaters in stairwells. Shipping included.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46632635859 | 1-LF7V843 | HVAC-Equipment | Material Only | Material Only Quote | Quoted | JONES LANG LASALLE AMERICAS INC | CDC2 - JONES LANG LASALLE - JPM | Y | 2017-02-09 15:52 | 29 | 1 to 30 | 21 to 30 | 0 | Scheduled | Pending Tech Acceptance | Branch Status | 2017-02-09 15:55 | 29 | 15 to 30 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | (NEED request id and work order) MATERIAL ONLY SR- 155 LBS OR REFRIGERANT PER KEVIN KELLY
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-41585574848 | 1-J3QZ6WW | HVAC-Equipment | L&M | Not To Exceed | Quoted | E I DUPONT | DUPONT CHESTNUT RUN | Y | 2016-10-27 17:21 | 134 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-10-27 17:21 | 134 | > 120 | 3891.73 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Johnson Controls Inc. will provide labor and material to perform the following; Building 713 Model number YLAA0115 Serial number 2GYM017106 1. Lockout system 1. 2. Remove refrigerant from system 1 and store in recovery tanks, weigh refrigerant recovered a
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-32680697625 | 1-F0H8RO9 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ASTRAZENECA PHARMACEUTICALS LP | Y | 2016-04-15 16:53 | 329 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-04-15 16:53 | 329 | > 120 | 1165 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | > 120 | Start-up/PCAT Labor¦1-Day - UNIT TRAINING
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-32680697811 | 1-F0H8RTF | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ASTRAZENECA PHARMACEUTICALS LP | Y | 2016-04-15 16:53 | 329 | > 120 | > 120 | 0 | Scheduled | Tech Accepted | Branch Status | 2016-04-15 16:53 | 329 | > 120 | 2000 | 0 | 0 | 0 | 0 | 0 | No WIP | 2016-06-17 | 266 | > 120 | > 120 | No | [9 empty] | CSTETST | > 120 | Start-up/PCAT Labor¦Humidifer cost repair-1/2 (UNIT STARTUP)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-32680923007 | 1-F0HDLKV | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ASTRAZENECA PHARMACEUTICALS LP | Y | 2016-04-15 16:54 | 329 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-04-15 16:54 | 329 | > 120 | 1400 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | > 120 | Truck Based Team Executed¦2% - REPAIR (Belt, Pulley Change, Modify Belt Guard)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-40683561505 | 1-IOTXWYP | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ATK BLDG C-33 | Y | 2016-09-23 14:02 | 168 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-09-23 14:02 | 168 | > 120 | 1920 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | > 120 | YCAL - Air Cooled Chiller - CH1¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-42856793230 | 1-JORTTAM | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ATK BLDG C-33 | Y | 2016-12-02 01:14 | 98 | 91 to 120 | 91 to 100 |  | Open | Unscheduled | Branch Status | 2016-12-02 01:14 | 98 | 91 to 120 | 1280 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 90 to 120 | DX Air Cooled Condensing Units - CU-1¦Start up/PCAT - Branch: Delmarva - 0260 in 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46708999753 | 1-LGHBYVD | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | EI DUPONT DE NEMOURS & CO | Y | 2017-02-13 15:39 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 15:39 | 25 | 15 to 30 | 583 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: 3 VFD (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709000201 | 1-LGHBZ7T | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | EI DUPONT DE NEMOURS & CO | Y | 2017-02-13 15:39 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 15:39 | 25 | 15 to 30 | 583 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: 3 VFD (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709000649 | 1-LGHBZK9 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | EI DUPONT DE NEMOURS & CO | Y | 2017-02-13 15:39 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 15:39 | 25 | 15 to 30 | 583 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: 3 VFD (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-41281623381 | 1-IYQ0GGL | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | JCI BATTERY DIVISION | Y | 2016-10-14 00:22 | 147 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-10-14 00:22 | 147 | > 120 | 1320 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | YLAA - Air Cooled Scroll Chiller - ACCH110¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2017
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46711468484 | 1-LGISVR8 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | KRAFT HEINZ DOVER, DE | Y | 2017-02-13 16:58 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 16:58 | 25 | 15 to 30 | 500 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | 1 to 90 | Solution XTI - AHU-021R-384¦Field Labor (except PCAT) - Factory Startup
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-41637583764 | 1-J4LXX90 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2016-10-29 14:16 | 132 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-10-29 14:16 | 132 | > 120 | 2640 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | > 120 | YLAA - Air Cooled Scroll Chiller - CH-1¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2017
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-41637675924 | 1-J4LZWD0 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2016-10-29 14:17 | 132 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-10-29 14:17 | 132 | > 120 | 2640 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | > 120 | YLAA - Air Cooled Scroll Chiller - CH-2¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2017
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709323851 | 1-LGHIWY3 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 | 1 | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:33 | 2 | 1 to 2 | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709324299 | 1-LGHIXAJ | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 | 1 | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:39 | 2 | 1 to 2 | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709327747 | 1-LGHIZYB | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 | 1 | Scheduled | Tech On Site | Branch Status | 2017-03-08 20:40 | 2 | 1 to 2 | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709328051 | 1-LGHJ06R | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 | 1 | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:41 | 2 | 1 to 2 | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709328499 | 1-LGHJ0J7 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 | 1 | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:41 | 2 | 1 to 2 | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709335803 | 1-LGHJ663 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:42 | 2 | 1 to 2 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709336251 | 1-LGHJ6IJ | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 | 1 | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:44 | 2 | 1 to 2 | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709336699 | 1-LGHJ6UZ | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 | 1 | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:44 | 2 | 1 to 2 | 349 | 126.17 | 0 | 0 | 4.5 | 130.67 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709348147 | 1-LGHJFOZ | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:46 | 2 | 1 to 2 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709348595 | 1-LGHJG1F | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:50 | 25 | 1 to 30 | 21 to 30 | 1 | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:47 | 2 | 1 to 2 | 349 | 126.17 | 0 | 0 | 0 | 126.17 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709357043 | 1-LGHJMK3 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:51 | 25 | 1 to 30 | 21 to 30 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:48 | 2 | 1 to 2 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46709357491 | 1-LGHJMWJ | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ROUTE 9 LIBRARY | Y | 2017-02-13 15:51 | 25 | 1 to 30 | 21 to 30 |  | Scheduled | Tech Accepted | Branch Status | 2017-03-08 20:49 | 2 | 1 to 2 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFD Startup (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47156712557 | 1-LNVW0A5 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | SEARS PRICES CORNER | Y | 2017-02-17 15:36 | 21 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-17 15:36 | 21 | 15 to 30 | 304 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | YCWL - Water Cooled Scroll Chiller - CH-2¦Connectivity - Connectivity - BACnet, Commissioning Labor, Installation Year: 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47156902126 | 1-LNW02JY | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | SEARS PRICES CORNER | Y | 2017-02-17 15:40 | 21 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-17 15:40 | 21 | 15 to 30 | 304 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | YCWL - Water Cooled Scroll Chiller - CH-2¦Connectivity - Connectivity - BACnet, Commissioning Labor, Installation Year: 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47156902605 | 1-LNW02X9 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | SEARS PRICES CORNER | Y | 2017-02-17 15:41 | 21 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-17 15:41 | 21 | 15 to 30 | 1900 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | YCWL - Water Cooled Scroll Chiller - CH-2¦Start up/PCAT - Branch: Philadelphia Service - 0607, Tier: 10 in 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47156903064 | 1-LNW03A0 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | SEARS PRICES CORNER | Y | 2017-02-17 15:42 | 21 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-17 15:42 | 21 | 15 to 30 | 1900 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | YCWL - Water Cooled Scroll Chiller - CH-2¦Start up/PCAT - Branch: Philadelphia Service - 0607, Tier: 10 in 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-34537671977 | 1-FV6U695 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | UNIVERSITY OF DELAWARE00514773 | Y | 2016-05-31 20:22 | 283 | > 120 | > 120 | 0 | Pending Adjustment | Pending Adjustment | Branch Status | 2016-10-07 18:09 | 154 | > 120 | 960 | 0 | 0 | 0 | 0 | 0 | No WIP | 2016-10-06 | 155 | > 120 | > 120 | No | [9 empty] | CDOLPHL | > 120 | DX Air Cooled Condensing Units - ACC-1_2¦Start up/PCAT - Branch: Delmarva - 0260 in 2016 SN 11531E64855064
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-43730886575 | 1-K388O1B | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | USPS NEW CASTLE | Y | 2016-12-28 21:48 | 72 | 61 to 90 | 71 to 80 |  | Open | Unscheduled | Branch Status | 2016-12-28 21:48 | 72 | 61 to 90 | 4166 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [10 empty] | 1 to 90 | YMC Chiller - CH-1¦Start up/PCAT - Branch: Philadelphia Service - 0607 in 2017¦Field Commissioning of Smart Chiller Equip Board
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45532648380 | 1-KX0YOCC | HVAC-Equipment | L&M | ROC Applications | Cost Transfers | BAYHEALTH MEDICAL KENT CAMPUS | BAYHEALTH MEDICAL KENT CAMPUS | Y | 2017-01-11 13:18 | 58 | 31 to 60 | 51 to 60 |  | Scheduled | Pending Tech Acceptance | Branch Status | 2017-01-11 13:53 | 58 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Operating Alarm ROC alarm / Acc. # 5364-7016-602925/ 650/ SEWM592210 To place a disregard for this or any other signal, call the ROC at 800-753-4524 Opt. 1 and supply the operator with the Acct Number listed above 01/11/2017 08:17:46 Chiller 2 Stopped
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-32802135464 | 1-F2HJLPK | HVAC-Equipment | L&M | ROC Applications | Cost Transfers | NEMOURS FOUNDATION | DUPONT HOSPITAL FOR CHILDREN | Y | 2016-04-20 01:00 | 324 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-04-20 01:00 | 324 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | > 120 | Connected Services Installation
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-41212886021 | 1-IXL36DH | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2016-10-11 13:05 | 150 | > 120 | > 120 |  | Open | Priority Dispatch AM | Branch Status | 2016-10-11 13:05 | 150 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Late to Test ROC alarm / Acc. # 5161-4266-452322/ / SET00108D0429DF Timestamp 10/11/2016 09:05:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-41362501991 | 1-J025YSN | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2016-10-18 12:51 | 143 | > 120 | > 120 |  | Open | Priority Dispatch AM | Branch Status | 2016-10-18 12:51 | 143 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Late to Test ROC alarm / Acc. # 5161-4408-464271/ / SET00108D0429DF Timestamp 10/18/2016 08:51:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-41441689859 | 1-J1DB8JN | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2016-10-21 13:09 | 140 | > 120 | > 120 |  | Open | Priority Dispatch AM | Branch Status | 2016-10-21 13:09 | 140 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Late to Test ROC alarm / Acc. # 5161-4457-468722/ / SET00108D0429DF Timestamp 10/21/2016 09:09:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-41520576322 | 1-J2OA1QA | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2016-10-25 13:28 | 136 | > 120 | > 120 |  | Scheduled | Tech Accepted | Branch Status | 2016-10-25 15:55 | 136 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Late to Test ROC alarm / Acc. # 5161-4495-474139/ / SET00108D0429DF Timestamp 10/25/2016 09:28:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-41915747637 | 1-J97JXV9 | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2016-11-09 13:58 | 121 | > 120 | > 120 |  | Open | Priority Dispatch AM | Branch Status | 2016-11-09 13:58 | 121 | > 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | Late to Test ROC alarm / Acc. # 5161-4558-499467/ / SET00108D0429DF Timestamp 11/09/2016 08:58:00 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-42119852862 | 1-JCL2MGU | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2016-11-12 14:16 | 118 | 91 to 120 | 111 to 120 |  | Open | Priority Dispatch AM | Branch Status | 2016-11-12 14:16 | 118 | 91 to 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 90 to 120 | Late to Test ROC alarm / Acc. # 5161-4594-503470/ / SET00108D0429DF Timestamp 11/12/2016 09:16:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-42426422070 | 1-JHNLGS6 | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2016-11-15 14:34 | 115 | 91 to 120 | 111 to 120 |  | Open | Priority Dispatch AM | Branch Status | 2016-11-15 14:34 | 115 | 91 to 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 90 to 120 | Late to Test ROC alarm / Acc. # 5161-4625-508092/ / SET00108D0429DF Timestamp 11/15/2016 09:34:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-42836944625 | 1-JOG0E0H | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2016-12-01 15:05 | 99 | 91 to 120 | 91 to 100 |  | Awaiting Internal Approval | Awaiting Internal Approval | Branch Status | 2016-12-01 16:36 | 99 | 91 to 120 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 90 to 120 | Late to Test ROC alarm / Acc. # 5161-4743-535746/ / SET00108D0429DF Timestamp 12/01/2016 10:05:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45876110740 | 1-L2PG9LG | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2017-01-25 16:30 | 44 | 31 to 60 | 41 to 50 |  | Open | Priority Dispatch AM | Branch Status | 2017-01-25 16:30 | 44 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Late to Test ROC alarm / Acc. # 5161-4898-625017/ / SET00108D0429DF Timestamp 01/25/2017 11:30:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46604456418 | 1-LER38PU | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2017-02-08 16:59 | 30 | 1 to 30 | 21 to 30 |  | Open | Priority Dispatch AM | Branch Status | 2017-02-08 16:59 | 30 | 15 to 30 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Late to Test ROC alarm / Acc. # 5161-4943-646664/ / SET00108D0429DF Timestamp 02/08/2017 11:59:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46684861701 | 1-LG2YLTX | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2017-02-11 17:17 | 27 | 1 to 30 | 21 to 30 |  | Open | Priority Dispatch AM | Branch Status | 2017-02-11 17:17 | 27 | 15 to 30 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Late to Test ROC alarm / Acc. # 5161-4976-652522/ / SET00108D0429DF Timestamp 02/11/2017 12:17:00 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46760357657 | 1-LHBWQVT | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2017-02-14 17:35 | 24 | 1 to 30 | 21 to 30 |  | Open | Priority Dispatch AM | Branch Status | 2017-02-14 17:35 | 24 | 15 to 30 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Late to Test ROC alarm / Acc. # 5161-5009-656302/ / SET00108D0429DF Timestamp 02/14/2017 12:35:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47714549796 | 1-LX40E90 | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2017-03-01 18:05 | 9 | 1 to 30 | 7 to 13 |  | Open | Priority Dispatch AM | Branch Status | 2017-03-01 18:05 | 9 | 8 to 14 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Late to Test ROC alarm / Acc. # 5161-5077-677877/ / SET00108D0429DF Timestamp 03/01/2017 13:05:02 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47851580982 | 1-LZDLG6U | HVAC-Controls | L&M | ROC Applications | Cost Transfers | UNIVERSITY OF DELAWARE | UNIVERSITY OF DELAWARE - CENTRAL PLANT | Y | 2017-03-04 18:23 | 6 | 1 to 30 | 4 to 6 |  | Open | Priority Dispatch AM | Branch Status | 2017-03-04 18:23 | 6 | 3 to 7 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | Late to Test ROC alarm / Acc. # 5161-5116-683495/ / SET00108D0429DF Timestamp 03/04/2017 13:23:01 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45659788401 | 1-KZ4NQ7L | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | DFAS-VD/L1 F67100 LIMESTONE | DELAWARE AIR NATIONAL GUARD | N | 2017-01-17 11:12 | 52 | 31 to 60 | 51 to 60 | 8 | Scheduled | Tech On Site | Branch Status | 2017-01-17 11:12 | 52 | 31 to 60 |  | 629.96 | 281.91 | 0 | -911.87 | 0 | No WIP | 2017-01-17 | 52 | 31 to 60 | 51 to 60 | No | [9 empty] | CDOLPHL | 1 to 90 | WARRANTY TO PROJECT
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-32327094311 | 1-EUMPTLZ | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | CDC1 - JONES LANG LASALLE - JPM | N | 2016-04-04 19:20 | 340 | > 120 | > 120 | 516.5 | Scheduled | Tech Accepted | Branch Status | 2016-04-04 19:20 | 340 | > 120 |  | 34467.41 | 443.01 | 0 | -34910.42 | 0 | No WIP | 2017-01-11 | 58 | 31 to 60 | 51 to 60 | No | [9 empty] | CDICKSM2 | > 120 | Project #6N280077 (Please post labor only - NO material orders) CDC EXHAUST
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-27605896846 | 1-COJU6BY | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | N | 2015-12-10 16:05 | 456 | > 120 | > 120 | 769.25 | Scheduled | Tech Accepted | Branch Status | 2015-12-10 16:05 | 456 | > 120 |  | 54940.74 | 591.09 | 0 | -55531.83 | 0 | No WIP | 2016-03-17 | 358 | > 120 | > 120 | No | [9 empty] | CDICKSM2 | > 120 | Project #5N280103 (labor only) VRF install
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-32234168004 | 1-ET3E37O | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | N | 2016-04-01 13:47 | 343 | > 120 | > 120 | 30 | Scheduled | Tech Accepted | Branch Status | 2016-04-01 13:47 | 343 | > 120 |  | 1596.82 | 0 | 0 | -1596.82 | 0 | No WIP | 2016-04-06 | 338 | > 120 | > 120 | No | [9 empty] | CDICKSM2 | > 120 | Project #5N280104 (labor only) Controls
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-33673837211 | 1-FGWJ72Z | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | N | 2016-05-02 17:07 | 312 | > 120 | > 120 | 733.75 | Scheduled | Tech Accepted | Branch Status | 2016-05-02 17:07 | 312 | > 120 |  | 56845.51 | 873.58 | 0 | -57719.09 | 0 | No WIP | 2017-01-13 | 56 | 31 to 60 | 51 to 60 | No | [9 empty] | CDOLPHL | > 120 | DANG BLDG 2902 Project #5N280107
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-38501911211 | 1-HOR1KTN | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | N | 2016-09-09 16:20 | 182 | > 120 | > 120 | 477 | Scheduled | Tech Accepted | Branch Status | 2016-09-09 16:20 | 182 | > 120 |  | 35905.59 | 526.95 | 0 | -36432.54 | 0 | No WIP | 2016-11-04 | 126 | > 120 | > 120 | No | [9 empty] | CDOLPHL | > 120 | PROJECT#6N28-0164; Veterans Design and Construction.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-43440239875 | 1-JYF73LV | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | N | 2016-12-23 14:51 | 77 | 61 to 90 | 71 to 80 | 9 | Scheduled | Tech Accepted | Branch Status | 2016-12-23 14:52 | 77 | 61 to 90 |  | 708.7 | 0 | 0 | -708.7 | 0 | No WIP | 2017-01-05 | 64 | 61 to 90 | 61 to 70 | No | [9 empty] | CDOLPHL | 1 to 90 | DAIKIN WARRANTY ISSUE - NEED MODEL AND SERIAL NUMBER
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47280239011 | 1-LPXFLWJ | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | DELAWARE AIR NATIONAL GUARD | N | 2017-02-22 20:52 | 16 | 1 to 30 | 14 to 20 | 6 | Scheduled | Tech Accepted | Branch Status | 2017-02-22 20:58 | 16 | 15 to 30 |  | 439.39 | 4.7 | 0 | -444.09 | 0 | No WIP | 2017-02-23 | 15 | 1 to 30 | 14 to 20 | No | [9 empty] | CDOLPHL | 1 to 90 | Daikin indoor fan making loud noise when running.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47831404653 | 1-LZ1L019 | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | DISCOVER FINANCIAL SERVICES | N | 2017-03-03 19:46 | 7 | 1 to 30 | 7 to 13 |  | Scheduled | Pending Tech Acceptance | Branch Status | 2017-03-03 19:48 | 7 | 3 to 7 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | 1 to 90 | COOLING TOWER ISSUE
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46705312394 | 1-LGF4XOQ | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | EMORY HILL REAL ESTATE SERVICES INC | N | 2017-02-13 13:52 | 25 | 1 to 30 | 21 to 30 | 211 | Scheduled | Tech Accepted | Branch Status | 2017-02-13 13:57 | 25 | 15 to 30 |  | 19910.57 | 0 | 0 | -17834.37 | 2076.2 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CDOLPHL | 1 to 90 | PROJECT 7N28-0053-LABOR ONLY(DISCOVER COOLING TOWER) 12 READS WAY, NEW CASTLE.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-43300943355 | 1-JW49HQ3 | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | HEDWIN CORPORATION - NEWARK DE | N | 2016-12-19 19:25 | 81 | 61 to 90 | 81 to 90 | 108 | Scheduled | Tech Accepted | Branch Status | 2016-12-19 19:26 | 81 | 61 to 90 |  | 8296.61 | 200.81 | 0 | -8497.42 | 0 | No WIP | 2017-01-05 | 64 | 61 to 90 | 61 to 70 | No | [9 empty] | CDOLPHL | 1 to 90 | LABOR ONLY. TO PURCHASE PARTS, USE 7N28-0038
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-29002126551 | 1-DBN482F | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | NEMOURS FOUNDATION | DUPONT HOSPITAL FOR CHILDREN | N | 2016-02-02 19:41 | 402 | > 120 | > 120 | 629.25 | In Progress | Returning For Completion | Branch Status | 2016-02-10 19:17 | 394 | > 120 |  | 52274.33 | 1316.79 | 0 | -53591.12 | 0 | No WIP | 2016-05-13 | 301 | > 120 | > 120 | No | [9 empty] | CDICKSM2 | > 120 | Project #6N280057
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-47263644901 | 1-LPNJXT1 | HVAC-Equipment | L&M | Warranty to Equipment | Warranty | BUILDING SYSTEMS & SERVICES (BUY/RESELL) | BUILDING SYSTEMS AND SERVICES, INC | N | 2017-02-22 14:18 | 16 | 1 to 30 | 14 to 20 | 0 | Scheduled | Pending Tech Acceptance | Branch Status | 2017-02-22 14:20 | 16 | 15 to 30 |  | 0 | 170.33 | 0 | 0 | 170.33 | Has WIP |  |  | No Labor | No Labor | No |  | Yes | 1 to 30 | [5 empty] | Open Claim | CDOLPHL | 1 to 90 | BSS REQUESTED WARRANTY PER MARK SHETTLE AMTRAK- WORTH & CO S/N N1K6020728 M/N J06ZFN12B4A1BAA1A1 UPG CLAIM J486210
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-46604691980 | 1-LER8AH8 | HVAC-Equipment | L&M | Warranty to Equipment | Warranty | DUPONT ACCOUNTS PAYABLE | DUPONT STINE HASKELL | N | 2017-02-08 16:53 | 30 | 1 to 30 | 21 to 30 | 5 | Scheduled | Pending Tech Acceptance | Branch Status | 2017-02-08 16:55 | 30 | 15 to 30 |  | 537.02 | 0 | 0 | -537.02 | 0 | No WIP | 2017-02-23 | 15 | 1 to 30 | 14 to 20 | Yes | 8K709006 | Yes | 1 to 30 | In Progress | 2017-02-08 16:56 | 30 |  |  | Pending NxGen Team | CDOLPHL | 1 to 90 | (claim updated and sent as complete 2/25) Model ylaa0070se46x Serial 11531c64654501 FREE COOLING ISSUES | 2017-03-09 | CHARGEDBACK PER BRANCH REQUEST.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-43184675622 | 1-JU71GYU | HVAC-Equipment | L&M | Warranty to Equipment | Warranty | GE AVIATION | GE AVIATION | N | 2016-12-15 20:28 | 85 | 61 to 90 | 81 to 90 | 11 | Scheduled | Tech Accepted | Branch Status | 2017-01-20 17:36 | 49 | 31 to 60 |  | 984.31 | 0 | 0 | -984.31 | 0 | No WIP | 2016-12-16 | 84 | 61 to 90 | 81 to 90 | Yes | 8K709001 | Yes | > 40 | Rejected | 2017-02-25 18:05 | 13 |  |  | Remove From Warranty | CDOLPHL | 1 to 90 | (resent claim 2/25 and email to Tim) a sd claim 8K709001. as of 1/7 PROGRESS-INACTIVE, BUT NOT REVIEWED OR CLASSIFIED NO HEAT S/N TDDM104900 | 2017-03-09 | CHARGEDBACK PER BRANCH REQUEST.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva North Team SVC | Service | 1-45383279350 | 1-KUK16GM | HVAC-Equipment | L&M | Warranty to Equipment | Warranty | GE AVIATION | GE AVIATION | N | 2017-01-05 13:32 | 64 | 61 to 90 | 61 to 70 | 7 | Scheduled | Tech Accepted | Branch Status | 2017-01-05 13:33 | 64 | 61 to 90 |  | 551.21 | 0 | 0 | -551.21 | 0 | No WIP | 2017-01-06 | 63 | 61 to 90 | 61 to 70 | Yes | 8K709002 | Yes | > 40 | Rejected | 2017-02-25 18:29 | 13 |  |  | Remove From Warranty | CDOLPHL | 1 to 90 | (updated SD with info 2/25). CUSTOMER STATES NO HEAT. ENTER PROBLEM, CAUSE AND SOLUTION. | 2017-03-09 | CHARGEDBACK PER BRANCH REQUEST.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47274943883 | 1-LPUA45N | HVAC-Equipment | L&M | Custom Quote | Quoted | CBRE | BB&T 152379 | Y | 2017-02-22 18:31 | 16 | 1 to 30 | 14 to 20 | 0 | Open | Unscheduled | Branch Status | 2017-02-22 18:31 | 16 | 15 to 30 | 4851.8 | 0 | 234 | 0 | 0 | 234 | Has WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | CBRE BB &T Millington, MD 2 ton Heat Pump Replacement. Provide Labor only. Duct transitions to adapt to new unit. Misc. material copper fittings, insulations, brazing rod, nitrogen. Labor: $4172.32 Materials: $483.79 Total: $4656.11 This
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47712376540 | 1-LX2PTCS | HVAC-Equipment | L&M | Custom Quote | Quoted | DELMAR SCHOOL DISTRICT | DELMAR SCHOOL DISTRICT | Y | 2017-03-01 15:16 | 9 | 1 to 30 | 7 to 13 | 0 | Scheduled | Tech Accepted | Branch Status | 2017-03-01 15:16 | 9 | 8 to 14 | 2300 | 0 | 673.94 | 0 | 0 | 673.94 | Has WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Compressor replacement for classroom C127
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47721695016 | 1-LX89JJC | HVAC-Equipment | L&M | Custom Quote | Quoted | M & T BANK | MANUFACTURERS AND TRADERS TRUST COMPANY | Y | 2017-03-01 19:23 | 9 | 1 to 30 | 7 to 13 | 0 | Scheduled | Tech Accepted | Branch Status | 2017-03-01 19:24 | 9 | 8 to 14 | 9588 | 0 | 3794.56 | 0 | 0 | 3794.56 | Has WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | To provide all labor and materials to bring back Fan in fan house #6 to excellent condition per scope of work set forth by M&T Bank and site supervisor Joe Weiser
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47460471026 | 1-LSWQLTE | HVAC-Controls | L&M | Custom Quote | Quoted | STATE OF MARYLAND DEPT OF GEN SVCS | DEERS HEAD HOSPITAL CENTER | Y | 2017-02-28 20:58 | 10 | 1 to 30 | 7 to 13 |  | Open | Unscheduled | Branch Status | 2017-02-28 20:58 | 10 | 8 to 14 | 3164.38 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Eddy current testing chiller 1 All testing will need to scheduled time of maintenance 1 drain and remove condenser head 2 remove and drain evaporator head 3 test each tube for deficiencies in report condition 4 install heads replace and refill chiller n
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47461723583 | 1-LSXHGAN | HVAC-Equipment | L&M | Custom Quote | Quoted | STATE OF MARYLAND DEPT OF GEN SVCS | DEERS HEAD HOSPITAL CENTER | Y | 2017-02-28 21:00 | 10 | 1 to 30 | 7 to 13 |  | Open | Unscheduled | Branch Status | 2017-02-28 21:00 | 10 | 8 to 14 | 3164.38 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Eddy current testing chiller 1 All testing will need to scheduled time of maintenance 1 drain and remove condenser head 2 remove and drain evaporator head 3 test each tube for deficiencies in report condition 4 install heads place system back in normal
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47725102871 | 1-LXAAL1Z | HVAC-Controls | L&M | Labor & Material | Non-Quoted |  | STATE OF DELAWARE | Y | 2017-03-01 20:38 | 9 | 1 to 30 | 7 to 13 | 8 | Scheduled | Tech Accepted | Branch Status | 2017-03-01 20:38 | 9 | 8 to 14 |  | 763.73 | 0 | 0 | 147.6 | 911.33 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CSTETST | 1 to 90 | One (1) JOHNSON CONTROLS METASYS Direct Digital Control System Furnish and install a JOHNSON CONTROLS METASYS Building Automation System to control the following material list per plans:: QTY DESCRIPTION 1 Air Cooled Chiller (existing controller)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47444970086 | 1-LSNID7Q | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | BEEBE MEDICAL CENTER | BEEBE MEDICAL CENTER AUXILIARY, INC. | Y | 2017-02-28 18:37 | 10 | 1 to 30 | 7 to 13 | 8 | Audit | Invoice Pending | BRC Status | 2017-03-02 22:08 | 8 | 8 to 14 |  | 683.35 | 0 | 0 | 45 | 728.35 | Has WIP | 2017-02-28 | 10 | 1 to 30 | 7 to 13 | No | [9 empty] | CSTETST | 1 to 90 | installing vgd valve on chiller 3 working on lean on chiller 1 looking at calibration on. Liquid level system 2
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46753378919 | 1-LH7R61Z | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | CHESAPEAKE REHABILITATION | REHABILITATION HOSPITAL CORPORATION OF AMERICA | Y | 2017-02-14 13:20 | 24 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-14 13:20 | 24 | 15 to 30 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Clean Boiler
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46567755694 | 1-LE58M9A | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | COUNTRY SCHOOL | THE COUNTRY SCHOOL INC | Y | 2017-02-07 13:31 | 31 | 31 to 60 | 30 to 40 | 4 | Scheduled | Tech Accepted | Branch Status | 2017-02-07 13:31 | 31 | 31 to 60 |  | 339.44 | 0 | 0 | 27 | 366.44 | Has WIP | 2017-02-07 | 31 | 31 to 60 | 31 to 40 | No | [9 empty] | CSTETST | 1 to 90 | Zone 6 pump 6 not running
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47308623255 | 1-LQEBZBR | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | HARRISON GROUP | HARRISON SUITES HOTEL | Y | 2017-02-23 20:14 | 15 | 1 to 30 | 14 to 20 | 0 | Scheduled | Tech Accepted | Branch Status | 2017-02-23 20:14 | 15 | 15 to 30 |  | 0 | 235.96 | 0 | 0 | 235.96 | Has WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Replace leaving water temp sensor and discharge sensor
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46763501372 | 1-LHDS4L8 | HVAC-Controls | L&M | Labor & Material | Non-Quoted | MEBA | THE CALHOON M E B A ENGINEERING SCHOOL ALUMNI ASSOCIATION INC | Y | 2017-02-14 16:57 | 24 | 1 to 30 | 21 to 30 | 7 | Scheduled | Tech Accepted | Branch Status | 2017-02-14 16:57 | 24 | 15 to 30 |  | 554.87 | 0 | 0 | 23.4 | 578.27 | Has WIP | 2017-03-06 | 4 | 1 to 30 | 4 to 6 | No | [9 empty] | CSTETST | 1 to 90 | Provide customer with six well mounted 8" temperature sensors and six stainless steel thermowells for their installation into predetermined pipe locations. Also provide an FEC controller, to be customer installed, for connection of sensors. Customer to pr
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-45472099250 | 1-KW0WWC2 | HVAC-Controls | L&M | Labor & Material | Non-Quoted | TALBOT COUNTY COURT HOUSE | COUNTY OF TALBOT | Y | 2017-01-09 13:29 | 60 | 31 to 60 | 51 to 60 |  | Open | Unscheduled | Branch Status | 2017-01-09 13:29 | 60 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Heat pumps not working
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-45875670573 | 1-L2P6TYL | HVAC-Controls | L&M | Labor & Material | Non-Quoted | TALBOT COUNTY COURT HOUSE | COUNTY OF TALBOT | Y | 2017-01-25 16:25 | 44 | 31 to 60 | 41 to 50 |  | Open | Unscheduled | Branch Status | 2017-01-25 16:25 | 44 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Check controls for boilers
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47163072769 | 1-LNZOBUP | HVAC-Controls | L&M | Labor & Material | Non-Quoted | TALBOT CTY BD OF EDUCATION | TALBOT COUNTY PUBLIC SCHOOLS | Y | 2017-02-17 19:48 | 21 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-17 19:48 | 21 | 15 to 30 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Check control for fuel pumps
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47905415694 | 1-M09NBBI | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | TALBOT CTY BD OF EDUCATION | TALBOT COUNTY PUBLIC SCHOOLS | Y | 2017-03-07 14:16 | 3 | 1 to 30 | 1 to 3 | 2 | Scheduled | Tech Accepted | Branch Status | 2017-03-07 14:16 | 3 | 3 to 7 |  | 169.72 | 0 | 0 | 22.5 | 192.22 | Has WIP | 2017-03-07 | 3 | 1 to 30 | 1 to 3 | No | [9 empty] | CSTETST | 1 to 90 | MOTON ELEMENTARY SCHOOL Pneumatic controls issues
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47978223275 | 1-M1GZU0B | HVAC-Controls | L&M | Labor & Material | Non-Quoted | UNIVERSITY OF MARYLAND | UMES-KIAH HALL | Y | 2017-03-09 18:17 | 1 | 1 to 30 | 1 to 3 | 8 | Scheduled | Tech Accepted | Branch Status | 2017-03-09 18:17 | 1 | 1 to 2 |  | 763.73 | 0 | 0 | 99 | 862.73 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CSTETST | 1 to 90 | Repairs due to flooding
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47238917340 | 1-LP8TXWC | HVAC-Controls | L&M | Labor & Material | Non-Quoted | UNIVERSITY OF MARYLAND MEDICAL SYSTEM | DORCHESTER GENERAL HOSPITAL INC | Y | 2017-02-21 16:54 | 17 | 1 to 30 | 14 to 20 |  | Open | Unscheduled | Branch Status | 2017-02-21 16:54 | 17 | 15 to 30 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | CANCER CENTER Replace DP sensor for AHU #1
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-45928602652 | 1-L3KPCM4 | HVAC-Equipment | L&M | Labor & Material | Non-Quoted | UNIVERSITY OF MARYLAND MEDICAL SYSTEM | MEMORIAL HOSPITAL OF EASTON, MD INC | Y | 2017-01-27 12:18 | 42 | 31 to 60 | 41 to 50 | 0 | In Progress | Unscheduled | Branch Status | 2017-01-31 16:05 | 38 | 31 to 60 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Materials for static pressure sensor on air handler performed on 1/17/17.
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46715980813 | 1-LGLHLHP | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | Y | 2017-02-13 19:33 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 19:33 | 25 | 15 to 30 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46715981004 | 1-LGLHLN0 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | Y | 2017-02-13 19:33 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 19:33 | 25 | 15 to 30 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46715981195 | 1-LGLHLSB | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | Y | 2017-02-13 19:34 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 19:34 | 25 | 15 to 30 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46715981386 | 1-LGLHLXM | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | Y | 2017-02-13 19:34 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 19:34 | 25 | 15 to 30 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46715981627 | 1-LGLHM4B | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | Y | 2017-02-13 19:37 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 19:37 | 25 | 15 to 30 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46716230828 | 1-LGLMYEK | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | ATLANTIC GENERAL HOSPITAL CORPORATION | Y | 2017-02-13 19:37 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 19:37 | 25 | 15 to 30 | 349 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Air Mod Start up/PCAT - (7253)¦0-75 Miles: VFDs (Year of Startup: 2016)
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-41337839761 | 1-IZNHDAP | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | DART FEDERALSBURG MD | Y | 2016-10-17 14:19 | 144 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-10-17 14:19 | 144 | > 120 | 4480 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CDOLPHL | > 120 | DX Indoor Scroll Chiller w/Remote Cond. - CH-1¦Start up/PCAT - Branch: Baltimore MD Service - 0319 in 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46419593673 | 1-LBP0ZPL | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | LAUREL ES | Y | 2017-02-01 14:26 | 37 | 31 to 60 | 30 to 40 |  | Open | Unscheduled | Branch Status | 2017-02-01 14:26 | 37 | 31 to 60 | 512 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | YVAA - Air Cooled Chiller - CH-2FINAL¦Connectivity - Connectivity - BACnet, Commissioning Labor, Installation Year: 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46420525302 | 1-LBPKYK6 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | LAUREL ES | Y | 2017-02-01 14:27 | 37 | 31 to 60 | 30 to 40 |  | Open | Unscheduled | Branch Status | 2017-02-01 14:27 | 37 | 31 to 60 | 1280 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | YVAA - Air Cooled Chiller - CH-2FINAL¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46711537214 | 1-LGIUCSE | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | LAUREL ES | Y | 2017-02-13 16:57 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 16:57 | 25 | 15 to 30 | 512 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | YLAA - Air Cooled Scroll Chiller - CH-1FINAL¦Connectivity - Connectivity - BACnet, Commissioning Labor, Installation Year: 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46711602113 | 1-LGIVQV5 | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | LAUREL ES | Y | 2017-02-13 16:57 | 25 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-13 16:57 | 25 | 15 to 30 | 1280 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | YLAA - Air Cooled Scroll Chiller - CH-1FINAL¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-37220863153 | 1-H3KC9TD | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | LOVE CREEK ELEMENTARY SCHOOL | Y | 2016-08-15 13:54 | 207 | > 120 | > 120 |  | Open | Unscheduled | Branch Status | 2016-08-15 13:54 | 207 | > 120 | 1280 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | > 120 | YVAA - Air Cooled Chiller - CH-1¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2016
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46545248534 | 1-LDRU7ME | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | SALISBURY UNIVERSITY CHILLER #2 | Y | 2017-02-06 17:09 | 32 | 31 to 60 | 30 to 40 | 10 | Scheduled | Tech Accepted | Branch Status | 2017-02-06 17:09 | 32 | 31 to 60 | 1980 | 1310.41 | 0 | 0 | 94 | 1404.41 | Has WIP | 2017-03-02 | 8 | 1 to 30 | 7 to 13 | No | [9 empty] | CSTETST | 1 to 90 | YVWA - Water Cooled Chiller - CH-2¦Start up/PCAT - Branch: Delmarva - 0260, Tier: 6 in 2017
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46912723987 | 1-LJUMHHV | HVAC-Equipment | L&M | PCAT Quoted | Startup | JCI US HVAC ES COMM SERV | SALISBURY UNIVERSITY CHILLER #2 | Y | 2017-02-15 19:05 | 23 | 1 to 30 | 21 to 30 |  | Open | Unscheduled | Branch Status | 2017-02-15 19:05 | 23 | 15 to 30 | 4000 | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | YVWA - Water Cooled Chiller - CH-2¦Field Labor (except PCAT) - 2 Yr Startup/Shutdown
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46692787779 | 1-LG7OHMR | HVAC-Controls | L&M | ROC Applications | Cost Transfers | M&E SALES | SALISBURY MIDDLE SCHOOL | Y | 2017-02-12 13:07 | 26 | 1 to 30 | 21 to 30 |  | Open | Priority Dispatch AM | Branch Status | 2017-02-12 13:07 | 26 | 15 to 30 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Late to Test ROC alarm / Acc. # 6160-4649-653349/ / SET00108D04A94B Timestamp 02/12/2017 08:07:00 The above account has lost all communication with the ROC and is not being monitored! This means that there is no communication between the NxE at your si
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47317062346 | 1-LQJCUYY | HVAC-Equipment | L&M | ROC Applications | Cost Transfers | SALISBURY UNIVERSITY | SALISBURY UNIVERSITY | Y | 2017-02-24 02:17 | 14 | 1 to 30 | 14 to 20 |  | Open | Priority Dispatch AM | Branch Status | 2017-02-24 02:17 | 14 | 8 to 14 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | Operating Alarm ROC alarm / Acc. # 6807-7593-669440/ 650/ SBCM166789 To place a disregard for this or any other signal, call the ROC at 800-753-4524 Opt. 1 and supply the operator with the Acct Number listed above 02/23/2017 21:16:25 CH-1 SYS 1 FAULT
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47920356064 | 1-M0IJJDS | HVAC-Equipment | L&M | ROC Applications | Cost Transfers | SALISBURY UNIVERSITY | SALISBURY UNIVERSITY | Y | 2017-03-07 23:57 | 3 | 1 to 30 | 1 to 3 | 4 | Scheduled | Tech Accepted | Branch Status | 2017-03-07 23:57 | 3 | 3 to 7 |  | 341.67 | 0 | 0 | 18 | 359.67 | Has WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CSTETST | 1 to 90 | Operating Alarm ROC alarm / Acc. # 6807-7676-687421/ 650/ SBCM166789 To place a disregard for this or any other signal, call the ROC at 800-753-4524 Opt. 1 and supply the operator with the Acct Number listed above 03/07/2017 18:56:33 CH-1 SYS 1 FAULT
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47920268136 | 1-M0IHNJC | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | BEEBE MEDICAL CENTER AUXILIARY, INC. | N | 2017-03-07 22:50 | 3 | 1 to 30 | 1 to 3 | 0 | Open | Unscheduled | Branch Status | 2017-03-07 22:50 | 3 | 3 to 7 |  | 0 | 0 | 0 | 0 | 0 | No WIP |  |  | No Labor | No Labor | No | [9 empty] | CSTETST | 1 to 90 | To invoice at cost for 2,935 pounds of R-134a for Beebe Medical Center
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46705065041 | 1-LGEZMTT | HVAC-Equipment | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | DISCOVER FINANCIAL SERVICES | N | 2017-02-13 13:32 | 25 | 1 to 30 | 21 to 30 | 6 | Scheduled | Tech Accepted | Branch Status | 2017-02-13 13:32 | 25 | 15 to 30 |  | 472.47 | 0 | 0 | -472.47 | 0 | No WIP | 2017-02-13 | 25 | 1 to 30 | 21 to 30 | No | [9 empty] | CSTETST | 1 to 90 | project 7N28-0017
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-46577469154 | 1-LEB0T7M | HVAC-Controls | L&M | Shared Resource to Projects | Cost Transfers | JCI US SS INTERCOMPANY SUBCONTRACT | LOWER EASTERN SHORE CHILDRENS CENTER | N | 2017-02-07 18:46 | 31 | 31 to 60 | 30 to 40 | 128 | Scheduled | Tech Accepted | Branch Status | 2017-02-07 18:46 | 31 | 31 to 60 |  | 7406.79 | 323.88 | 0 | -7730.67 | 0 | No WIP | 2017-03-09 | 1 | 1 to 30 | 1 to 3 | No | [9 empty] | CSTETST | 1 to 90 | Project #5N270298
2017-03-10 | East Region | East1 SubRegion | 0N28 | JOHNSON CONTROLS SALISBURY WILMINGTON CB - 0N28 | 260 Delmarva South Team SVC | Service | 1-47867047924 | 1-LZMSYK4 | HVAC-Equipment | L&M | Warranty to Equipment | Warranty | OHIO CAT | OHIO CAT | N | 2017-03-06 08:20 | 4 | 1 to 30 | 4 to 6 | 6 | Scheduled | Scheduled After Hours | Branch Status | 2017-03-06 09:00 | 4 | 3 to 7 |  | 684.51 | 2776 | 0 | -3460.51 | 0 | No WIP | 2017-03-06 | 4 | 1 to 30 | 4 to 6 | Yes | 8T716013 | Yes | 1 to 30 | In Progress | 2017-03-06 16:41 | 4 |  |  | Pending NxGen Team | CSTETST | 1 to 90 | Loc: Perdue, 6906 Zion Church Rd, Salisbury, MD 21804 Due: 3/6/17 Emg Desc: 100 ton rental chiller shut down on motor pressure high pressure cut out and low suction pressure Update 6am : Compressor was found to have blown up and needs to be repl | 2017-03-06 | Extended Warranties on Claim :