## output-1.csv
Opened | SR # | Customer PO# | Description | Contact Last | Opened | Modified | Closed | Status | Substatus | Date Committed
2016-11-16 11:35 | 1-42462980933 | 6501663924 | CHILLERS #8, #9, #10 SOFTWARE UPGRADE: Coordinate with DuPont Operators to Shutdown and Lockout one Chiller at a time UPGRADE all three CHILLER MICROBOARDs to the LATEST Revision of CONTROL LOGIC SOFTWARE (v. C.03F.03) Unlock, Start Up, and Verify CHILLER Control Operation, and Ensure proper Communication with MICROGATEWAY Modbus Interface Chillers #8 and #9 are currently running with the Original Software C.03F.00 Chiller #10 is currently running Software Version C.03F.01 | Cozza | 2016-11-16 11:35 | 2016-11-30 15:00 | 2016-11-30 15:00 | Closed | Closed | 2016-11-18 11:35
2016-10-26 15:42 | 1-41561145038 | 6501611952 | ABSORBERS #2 & #3 PROVIDE MATERIAL: LITHIUM MOLYBDATE INHIBITOR based on recent SOLUTION Analysis to bring Levels back to Optimal. *Inhibitor levels in ABSORBERS #1 & #4 are within the Normal range and do not need adjustment at this time.* | Cozza | 2016-10-26 15:42 | 2016-11-08 15:39 | 2016-11-08 15:39 | Closed | Closed | 2016-10-28 15:42
2016-08-25 11:02 | 1-37498214070 | 6501630558 | ABSORBER #1 "AUTO-PURGE FAILURE" Troubleshooting, Leak Test & Repairs: Completely DISASSEMBLE Purge Header REMOVE and REPLACE Faulty Solenoid Valve (1SOL) CLEAN all PIPING and THREADS DISASSEMBLE Automatic Ball Valve (2SOL) CLEAN and Re-Assemble RE-ASSEMBLE all PIPING w/ New Sealant and Flange Gasket. REPLACE PURGE CHECK VALVE and TRANSDUCER PRESSURIZE Purge Header and Verify that it is Leak Free and Dry Return Auto-Purge Operation to "AUTOMATIC" | Cozza | 2016-08-25 11:02 | 2016-08-29 12:48 | 2016-08-29 12:48 | Closed | Closed | 2016-08-27 11:02
2016-08-03 12:06 | 1-36853244088 | 6501620987 | ABSORBER #3 Due to the HIGH FREQUENCY of PURGES while Operational, along with CHEMICAL ANALYSIS, Recommend INSTALLING LITHIUM NITRATE TYPE INHIBITOR Perform LEAK TEST of PURGE TREE HEADER and REPAIR any LEAKS FOUND ABSORBER #3 should REMAIN OPERATING in order to properly TREND PURGE FREQUENCY, and determine if there are other possible causes | Cozza | 2016-08-03 12:06 | 2016-08-26 09:50 | 2016-08-26 09:50 | Closed | Closed | 2016-08-05 12:06
2016-07-20 13:54 | 1-36363184896 | 6501616658 | ABSORBER #1 Due to High Concentration of Suspended Solids after Solution Pump Failure, FILTERING is REQUIRED RELOCATE Canister from ABS#2 to ABS#3 INSTALL NEW HOSES, FLANGE and BALL VALVE (on VP7) FURNISH 18 New PALL Bromide Solution FILTERS to REPLENISH Supply onsite. (6 Filters per Changeout) REMOVE and REPLACE current clogged Filters CLEAN out Canister EVACUATE and RETURN to Service REPLACE FILTERS as needed until SUSPENDED SOLIDS in SOLUTION is at ACCEPTABLE LEVELS | Cozza | 2016-07-20 13:54 | 2016-08-31 08:10 | 2016-08-31 08:10 | Closed | Closed | 2016-07-22 13:54
2016-07-07 11:09 | 1-35974893871 | 6501611959 | ABSORBER #3 REMOVE and REPLACE Faulty Solenoid Valve (1SOL) CLEAN Purge Header Return Purge Operation back to AUTOMATIC OPERATORS will no longer need to worry about MANUALLY Purging PURGE TANK | Cozza | 2016-07-07 11:09 | 2016-07-22 10:05 | 2016-07-22 10:05 | Closed | Closed | 2016-07-09 11:09
2016-07-06 11:15 | 1-35942212834 | 6501611952 | ABSORBERS #2, #3, #4 LITHIUM MOLYBDATE INHIBITOR based on recent SOLUTION Analysis to bring Levels back to Optimal. | Cozza | 2016-07-06 11:15 | 2016-07-22 10:14 | 2016-07-22 10:14 | Closed | Closed | 2016-07-08 11:15
2016-07-05 11:19 | 1-35911259064 | 6501611969 | ABSORBER #1 Furnish NEW Motor Assembly for the Main Solution Pump (This is the entire Pump with exception on the Volute and Impeller) ** The cost of installing the Pump and all Labor associated with bringing ABSORBER #1 back online will be covered by the original JCI Quote # 1-G8EH8ER. ** ** For the price of both Quotes, DuPont will have 1 NEW Solution Pump w/Motor Installed & 1 Rebuilt Solution Pump w/Motor, left onsite as a Spare ** **** Lead Time for the NEW Motor Assembly from the Factory is currently 3 Weeks **** | Cozza | 2016-07-05 11:19 | 2016-07-22 09:59 | 2016-07-22 09:59 | Closed | Closed | 2016-07-07 11:19
2016-06-23 12:42 | 1-35376456034 | 6501608975 | ABSORBER #1 Remove and Replace Main Solution Pump Wearing Rings Remove and Replace Seized Studs in Pump Casing Thoroughly Clean all Pump Parts Furnish and Install New Pump Motor Carbon Graphite Bearings Re-Assemble Pump with Original Impeller Re-Install Pump with New Casing Gasket Install new Motor Contactor and Overload Assembly and Re-wire the pump Remove and Replace Fouled Sight-glasses in Absorber Section Evacuate Absorber Re-Install removed Solution through Filters Reset Valves to Original Positions Startup and Purge Absorber Ensure proper Operation | Cozza | 2016-06-23 12:42 | 2016-07-29 08:50 | 2016-07-29 08:50 | Closed | Closed | 2016-06-25 12:42
2016-06-20 13:06 | 1-35270891278 | 6501605952 | ABSORBER #1 Machining will be performed on the Main Solution Pump Rotor Assembly to repair worn parts and return to design specs. Have Impeller Balance verified. (If unbalanced an additional quote will be provided). | Cooper | 2016-06-20 13:06 | 2016-06-30 18:55 | 2016-06-30 18:55 | Closed | Closed | 2016-06-22 13:06
2016-06-09 07:09 | 1-34850489163 | 6501600380 | ABSORBER#1 MAIN SOLUTION PUMP INSPECTION Transfer Solution to Generators and Drums Disconnect and Pull Main Solution Pump Inspect, Clean out Solution, Disassemble Pump Inspect Bearings, Impeller, and Pump Seals Install Blank on Pump Volute until Additional Repairs are made | Cozza | 2016-06-09 07:09 | 2016-06-20 10:14 | 2016-06-20 10:14 | Closed | Closed | 2016-06-11 07:09
2016-02-12 08:44 | 1-29274542300 | 6501549099 | Remove samples of compressor oil and refrigerant for chemical analysis. Refrigerant leak test chiller and document leaks found (repair “minor” leaks, if possible). Transfer R-134A to storage tank for accurate weight of charge (Leaving 5psi on Chiller). Furnish and change compressor oil filters, and all driers. Furnish and change gearbox oil filters and oil (*Gear/Motor Oil furnished by DuPont*). Inspect gears and internal gearbox components. Disassemble motor coupling and check cold alignment. Repack motor coupling with grease and reassemble. Disassemble Compressor coupling. Check compressor axial thrust readings. Check compressor coupling cold alignment. Reassemble coupling. Vacuum out compressor motor. Brush clean all oil cooler tubes (Gear & Compressor). Transfer R-134A charge back into Chiller. | Cozza | 2016-02-12 08:44 | 2016-04-14 08:53 | 2016-04-14 08:53 | Closed | Closed | 2016-02-14 08:44
2016-02-04 14:11 | 1-29066059613 | 6501545663 | Eddy-Current Testing performed on all Evaporator (1852) and Condenser (2590) Tubes. Detailed report of analysis will be provided to DuPont. Water Box Heads must be removed, all tubes thoroughly cleaned, and scaffolding set up, before technician arrives | Cozza | 2016-02-04 14:11 | 2016-03-09 09:06 | 2016-03-09 09:06 | Closed | Closed | 2016-02-06 14:11
2016-02-02 12:47 | 1-28998918974 | 6501541957 | Complete replacement of faulty and obsolete Compressor Pneumatic Vane Actuator w/ integral Pilot Positioner. (The new actuator is the latest model of its kind, thereby making replacements parts readily available in the future.) Replace control air pressure throttling valve. Replace any pneumatic tubing or fittings necessary. Replace pneumatic air filters on for control air and main piston air. Set pressure regulators to design pressures. Set up correct position stroke length and span. Calibrate controls for proper Vane positioning and stable control of Compressor. Check control and operation of both Interstage and Hot Gas Bypass Bypass valves. Ensure that the are working as per design and in conjunction with Vane Actuator. | Cozza | 2016-02-02 12:47 | 2016-03-29 12:53 | 2016-03-29 12:53 | Closed | Closed | 2016-02-04 12:47
2016-01-21 13:40 | 1-28657093467 | 6501537307 | Furnish qty-4 rolls of gasket material p/n 028-03242-050. Shipping included. | Cooper | 2016-01-21 13:40 | 2016-01-25 13:45 | 2016-01-25 13:45 | Closed | Closed | 2016-01-23 13:40
2016-01-18 20:56 | 1-28577700955 | 6501537148 | CHILLER #7 Capacity Control Inspection, Diagnosis, and Evaluation of any Repairs Necessary. - This work is in response to DuPont Powerhouse Operators reporting erratic operation of Chiller #7's Capacity Control Pre-Rotation Vanes and a Vibration Shutdown Fault. - If substantial repairs are determined to be necessary, a separate quote will be provided to cover the additional Labor and Materials involved. | Cozza | 2016-01-18 20:56 | 2016-01-25 17:38 | 2016-01-25 17:38 | Closed | Closed | 2016-01-20 20:56
2015-11-05 08:43 | 1-26693184827 | 6501505894 | Molybdate Corrosion Inhibitor in quantities specified by recent Lithium Bromide lab analysis for each ABSORBER. *This quote is for MATERIAL ONLY. Labor for adding Inhibitor will be covered under the current Maintenance Contract.* | Cozza | 2015-11-05 08:43 | 2015-11-10 16:56 | 2015-11-10 16:56 | Closed | Closed | 2015-11-07 08:43
2015-10-30 13:08 | 1-26526940839 |  | Replace defective Purge Solenoid Valves (1SOL) on ABSORBER #1 and ABSORBER #2. Current valves were not properly sealing when closed, causing the Absorber Logic Board to cease "Smart" Auto-Purge Operation, and requiring Operators to Manually purge the Purge Tank while in Absorbers are in operation. Return Purges to Auto-Mode and Inspect Operation. **Quote DOES NOT include the price of the New Solenoid Valves. These were already purchased and billed to DuPont on a previous job.** | Cozza | 2015-10-30 13:08 | 2015-11-02 12:47 | 2015-11-02 12:47 | Closed | Closed | 2015-11-01 13:08
2015-09-24 07:50 | 1-25343174313 | 6501485253 | Furnish qty-12 York Oil Filters p/n 025-11225-000 Shipping included | Cooper | 2015-09-24 07:50 | 2015-10-01 18:33 | 2015-10-01 18:33 | Closed | Closed | 2015-09-26 07:50
2015-08-17 16:11 | 1-24187391580 | 6501469316 | YORK Parts ONLY for ABSORBER #4 (All Parts are New and should be Replaced when Motor/Rotor/Impeller Assembly is pulled): Refrigerant Pump Motor Motor Front and Rear Bearings Pump Casing Wearing Ring Motor Side Wearing Ring Impeller Fastening Hardware Pump Casing Gasket Motor Contactor & Overload Assembly All parts are available at are Baltimore Parts Center in Limited Quantities. | Cozza | 2015-08-17 16:11 | 2015-10-05 15:23 | 2015-10-05 15:23 | Closed | Closed | 2015-08-19 16:11
2015-05-07 09:00 | 1-20798887284 | 6501426534 | Furnish qty-1 55 gallon drum of new York "K" oil. Shipping included. | Cozza | 2015-05-07 09:00 | 2015-05-26 14:11 | 2015-05-26 14:11 | Closed | Closed | 2015-05-09 09:00
2015-05-06 13:35 | 1-20772877187 | 6501426354 | Supply 36 Solution filters for Absorber #2. | Cozza | 2015-05-06 13:35 | 2015-05-27 14:11 | 2015-05-27 14:11 | Closed | Closed | 2015-05-08 13:35
2015-02-06 09:38 | 1-18202458640 | LOX611091 | Furnish and install qty-1 new compressor shaft seal on Chiller #7. m/n OM3000 s/n MRP626904 Lock out / Tag out all energy sources Recover refrigerant into chiller reciever Disconnect coupling between gearbox and compressor Check and record compressor alignment readings Check and record compressor axial thrust reading Install new compressor shaft seal Reassemble compressor coupling Pressure test and evacuate chiller Recharge chiller with recovered refrigerant Exclusions: Additional refrigerant charge if needed Leak repairs other than compressor shaft seal | Cozza | 2015-02-06 09:38 | 2015-03-20 08:54 | 2015-03-20 08:54 | Closed | Closed | 2015-02-08 09:38
2015-01-23 15:31 | 1-17767611385 | LOX610743 | Material Only - Provide (6) 392 10719 000 KIT, FILTER and (6) 028 08312 001 KIT, REPL GASKETS | Cozza | 2015-01-23 15:31 | 2015-01-30 19:44 | 2015-01-30 19:44 | Closed | Closed | 2015-01-25 15:31
2015-01-16 08:49 | 1-17578850663 | LOX610534 | Furnish and install qty-4 new transducers and qty-8 new temperature sensors on Chiller #9. Connect all wiring and verify operation of each device. | Cozza | 2015-01-16 08:49 | 2015-04-09 08:46 | 2015-04-09 08:44 | Closed | Closed | 2015-01-18 08:49
2014-12-10 13:05 | 1-16741327980 | LOX609895 | Furnish gasket material for York Absorption chillers. qty-300 ft of Bulb gasket material qty-25 ft of baffle gasket material | Cooper | 2014-12-10 13:05 | 2014-12-17 14:18 | 2014-12-17 14:18 | Closed | Closed | 2014-12-12 13:05
2014-10-15 14:20 | 1-15112969639 | LOX608468 | Parts only. Provide Two Three way Valves for the installation of dual relief valves on Chiller #8 and #9 | Cozza | 2014-10-15 14:20 | 2014-11-13 10:58 | 2014-11-13 10:57 | Closed | Closed | 2014-10-17 14:20
2014-10-15 14:14 | 1-15112209612 | LOX608467 | Provide Corrosion Inhibitor for the Absorption Chillers Per the Solution Analysis. Provide the labor to charge the inhibitor into the Absorbers. | Cozza | 2014-10-15 14:14 | 2014-11-04 10:53 | 2014-11-04 10:53 | Closed | Closed | 2014-10-17 14:14
2014-03-26 11:18 | 1-9687624328 | LOX597574 | INCLUDED • Disassemble and remove existing Pin Relief Valve. • Provide and install a 3 Way Isolation valve • Provide and install two rupture disk and Disk Holders. • Provide new Gaskets and Bolts Reinstall Spring loaded relief disks after the rupture disks. NOT INCLUDED • Piping modifications needed to connect out of the dual relief assembly to the common header • New spring relief Valve Partial Billing of $13016.54 PO from Dupont Remaining amount of $4000.00 will be billed when valves come in | Skilton | 2014-03-26 11:18 | 2014-04-17 13:38 | 2014-03-26 15:57 | Closed | Closed | 2014-03-28 11:18
2014-03-13 13:03 | 1-9416568627 | LGGC21128 | Replace all Transducers and Temperature Sensors on CH 10 Order a backup set of sensors and transducers for spare parts. | Cozza | 2014-03-13 13:03 | 2014-03-24 13:28 | 2014-03-24 13:28 | Closed | Closed | 2014-03-15 13:03
2014-03-06 09:48 | 1-9307117648 | LOX600371 | Furnish qty-1 55 gallon drum of new York "J" oil. Furnish qty-3 5 gallon containers of new York "J" oil. Shipping included. Pricing: York "J" oil 5 gallon container $756.00 each. York "J" oil 55 gallon container $8,427.00 | Skilton | 2014-03-06 09:48 | 2014-03-19 10:28 | 2014-03-19 10:28 | Closed | Closed | 2014-03-08 09:48
2014-02-14 11:34 | 1-8972377924 | LGGC20932 | Tube Plugging during Eddy Current Test on the Evaporator Tubes CH#6 | Cozza | 2014-02-14 11:34 | 2014-02-19 08:44 | 2014-02-19 08:44 | Closed | Closed | 2014-02-16 11:34
2014-02-12 11:16 | 1-8936306112 | LOX598048 | Eddy Current test the condenser and sub cooler tubes on Chiller #6 Provide a detailed report on the condition of the tubes The tubes must be cleaned prior to testing. Exclusions Tube cleaning Tube Plugging | Cozza | 2014-02-12 11:16 | 2014-02-19 10:09 | 2014-02-19 10:09 | Closed | Closed | 2014-02-14 11:16
2014-02-04 14:11 | 1-8817876517 | LOX598757 | Perform Eddy Current Test on the Evaporator Tubes CH#6 Provide a detailed report of the test Tubes must be cleaned prior to testing Exclusions Tube Cleaning Tube Plugging Head Removal | Cozza | 2014-02-04 14:11 | 2014-02-18 13:11 | 2014-02-18 13:11 | Closed | Closed | 2014-02-06 14:11
2014-01-21 08:42 | 1-8552733559 | LOX597975 | * Mobilize/lock out equipment *Recover Refrigerant *Dissassemble and Inspect Compressor. Record Existing Tolerances *Reassemble Compressor with new bearings, seals, and gaskets *Realign motor to compressor *Pressure test and leak test the unit *Evacuate and recycle the refrigerant into the unit *Start, Teat and Adjust Not Included *Additional Refrigerant *Required Scaffolding | Cozza | 2014-01-21 08:42 | 2014-03-26 10:00 | 2014-03-26 10:00 | Closed | Closed | 2014-01-23 08:42
2014-01-10 09:10 | 1-8412597585 | Raul Cozza | *Eddy current test the condenser tubes * Provide report on the condition of the tubes * Tubes must be cleaned prior to the test Exclusions Tube cleaning Head removal Tube plugging | Cozza | 2014-01-10 09:10 | 2014-02-11 10:51 | 2014-02-11 10:51 | Closed | Closed | 2014-01-12 09:10
2014-01-08 07:28 | 1-8363544161 | LOX597574 | INCLUDED • Disassemble and remove existing Pin Relief Valve. • Provide and install a 3 Way Isolation valve • Provide and install two rupture disk and Disk Holders. • Provide new Gaskets and Bolts Reinstall Spring loaded relief disks after the rupture disks. NOT INCLUDED • Piping modifications needed to connect out of the dual relief assembly to the common header • New spring relief Valve | SLIWINSKI | 2014-01-08 07:28 | 2014-04-24 11:10 | 2014-04-24 11:10 | Closed | Closed | 2014-01-10 07:28
2013-10-02 12:58 | 1-7265537958 | LOX589867 | Furnish Lithium Molybdate inhibitor in qty-3 absorption chillers as needed based on analysis results. | SLIWINSKI | 2013-10-02 12:58 | 2013-10-31 10:05 | 2013-10-31 10:05 | Closed | Closed | 2013-10-04 12:58
2013-07-10 08:41 | 1-6950972053 | LOX591186 | Add lithium Bromide to absorber #2 | Sliwinski | 2013-07-10 08:41 | 2016-04-20 08:02 | 2016-04-20 08:02 | Closed | Closed | 2013-07-12 08:41
2013-06-18 10:53 | 1-6869910154 | LOX590515 | Furnish Lithium Molybdate inhibitor in qty-3 absorption chillers as needed based on analysis results. | SLIWINSKI | 2013-06-18 10:53 | 2013-06-25 11:48 | 2013-06-25 11:48 | Closed | Closed | 2013-06-20 10:53
2013-04-29 08:55 | 1-6696323989 | LOX588443 | Proposal to plug chiller 9 and chiller 10 | SLIWINSKI | 2013-04-29 08:55 | 2013-05-01 14:35 | 2013-05-01 14:34 | Closed | Closed | 2013-05-01 08:55
2013-04-17 14:12 | 1-6662123802 | LOX583374 | Provide eddycurrent testing on all condenser and evaporator tubes on chillers #8, 9, and 10. Note: Head removal and tube cleaning provided by others. CH-8 m/n OTT4G2-ZBES s/n GACM117864 CH-9 m/n OTT4G2-ZBES s/n GACM127698 CH-10 m/n OTT4G2-ZBES s/n GACM127699 | SLIWINSKI | 2013-04-17 14:12 | 2013-04-30 15:14 | 2013-04-30 15:14 | Closed | Closed | 2013-04-19 14:12
2013-02-28 13:05 | 1-6482766674 | LOX585576 | Rupture disk replacement Chiller 8 and two spare disks. 8 hours labor to include: Three Disks One Disk Holder | SLIWINSKI | 2013-02-28 13:05 | 2013-08-19 13:28 | 2013-08-19 13:28 | Closed | Closed | 2013-03-02 13:05
2013-02-25 09:10 | 1-6465393059 | LOX585468 | Furnish qty-1 55 gallon container of York "K" oil | SLIWINSKI | 2013-02-25 09:10 | 2013-03-06 15:12 | 2013-03-06 15:12 | Closed | Closed | 2013-02-27 09:10
2013-01-16 08:44 | 1-6308784998 | LOX583896 | Budgetary proposal to rebuild compressor on Chiller #8. m/n OTT4G2-ZBES s/n GACM117864 Lock out / tag out all energy sources Recover and store all refrigerant using plant recovery system Disconnect compressor coupling Disconnect all compressor piping Set up rigging and lower compressor to ground Record compressor thrust and runout readings Disassemble entire compressor and evaluate all parts Furnish and install new compressor bearings and gaskets Record compressor thrust and runout readings after rebuild Rig compressor onto chiller Reconnect all piping Pressure test system with nitrogen and leak test Check and adjust motor alignment as needed Reassemble compressor coupling Evacuate system and charge with recovered refrigerant Run chiller and check operation Provide all documentation Note: Pricing per chiller. 50,066.00 | SLIWINSKI | 2013-01-16 08:44 | 2013-02-12 13:02 | 2013-02-12 13:02 | Closed | Closed | 2013-01-18 08:44
2012-11-19 08:58 | 1-6073656448 | LOX581421 | MATERIAL ONLY Furnish qty-1 55 gal. drum of York "K" oil | SLIWINSKI | 2012-11-19 08:58 | 2013-02-12 13:01 | 2013-02-12 13:01 | Closed | Closed | 2012-11-21 08:58
2012-08-29 07:48 | 1-5710749030 | LDFS25135 | PARTS ORDER DuPont Experimental Station Absorber #2 m/n YPCST226-46-CXA s/n GADM248980 •Furnish and install qty-1 new absorber pump impeller. •Run unit and check operation. | SLIWINSKI | 2012-08-29 07:48 | 2012-09-26 17:11 | 2012-09-26 17:11 | Closed | Closed | 2012-08-31 07:48
2012-08-02 10:08 | 1-5591819781 | LGGC16834 | Repair Absorber #2 Solution Pump. Furnish and install qty-1 new pump motor with repair kit. Furnish and install qty-1 new pump overload relay Furnish and install qty-1 new pump contactor. Start pump and check operation. | SLIWINSKI | 2012-08-02 10:08 | 2012-09-14 10:46 | 2012-09-14 10:46 | Closed | Closed | 2012-08-04 10:08
2012-06-12 10:07 | 1-5326338169 | LGGC16318 | Use PO LGGC16318 DuPont Experimental Station Wilmington, DE •Furnish and install Lithium Molybdate inhibitor in qty-4 absorption chillers as needed based on analysis results. | SLIWINSKI | 2012-06-12 10:07 | 2012-09-14 11:09 | 2012-09-14 11:09 | Closed | Closed | 2012-06-14 10:07
2012-06-05 08:32 | 1-5291903176 | LOX574005 | Use PO # LOX574005 •Furnish qty-2 new purge transducers p/n 025-29907-002. | SLIWINSKI | 2012-06-05 08:32 | 2012-06-28 14:34 | 2012-06-28 14:34 | Closed | Closed | 2012-06-07 08:32
2012-05-25 08:19 | 1-5238056088 | LGGC16094 | DuPont Experimental Station Absorber #3 m/n YPCST226-46-CXA s/n GADM233620 •Respond to service call on unit shutting down on “High first stage generator temperature”. •Run unit through de-crystallization procedure. •Apply external heat to liquefy stubborn areas. •Run unit and check operation. | Sliwinski | 2012-05-25 08:19 | 2012-05-30 12:39 | 2012-05-30 12:39 | Closed | Closed | 2012-05-27 08:19
2012-04-03 08:32 | 1-4972943318 | LGGC15615 | USE PO# LGGC15615 Chiller #10 Job Scope: Furnish and install qty-1 Norris Valve seal kit. •Lock out / Tag out all energy sources. •Furnish and install qty-1 valve O-ring kit for free cooling valve. •Pressurize and leak check new valve. •Clean up chiller. •Check operation. •Note: Refrigerant recovery and recharge performed by others. | Sliwinski | 2012-04-03 08:32 | 2013-06-24 14:22 | 2013-06-24 14:22 | Closed | Closed | 2012-04-05 08:32
2012-04-03 08:27 | 1-4972942980 | LGGC15614 | Use PO#LGGC15614 Chiller #9 Job Scope: Furnish and install qty-1 Norris Valve seal kit. •Lock out / Tag out all energy sources. •Furnish and install qty-1 valve O-ring kit for free cooling valve. •Pressurize and leak check new valve. •Clean up chiller. •Check operation. •Note: Refrigerant recovery and recharge performed by others. | Sliwinski | 2012-04-03 08:27 | 2012-09-14 11:02 | 2012-09-14 11:02 | Closed | Closed | 2012-04-05 08:27
2012-03-12 09:02 | 1-4856238148 | LGGC15395 | Use PO#LGGC15395 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 Norris Valve seal kit. •Lock out / Tag out all energy sources. •Furnish and install qty-1 valve O-ring kit. •Pressurize and leak check new valve. •Check operation. | SLIWINSKI | 2012-03-12 09:02 | 2012-09-14 10:55 | 2012-09-14 10:55 | Closed | Closed | 2012-03-14 09:02
2012-02-29 13:13 | 1-4794930239 | LGGC14985 | THIS IS 2 OF 2 ( PARTIAL BALANCE ) Original SR 1-4712912261 has been billed for $12,000.00 USE PO# LGGC14985 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. •Lock out / Tag out all energy sources. •Recover and weigh entire refrigerant charge using plant recovery system. •Disassemble compressor coupling. •Remove and replace compressor shaft seal. •Leak test entire chiller with nitrogen. •Evacuate chiller and perform vacuum hold test. •Check coupling alignment using laser alignment tool. •Reassemble compressor coupling. •Charge chiller with recovered refrigerant. •Furnish and install 20 gallons of new compressor oil. •Run chiller and check operation. | Sliwinski | 2012-02-29 13:13 | 2012-03-27 14:30 | 2012-03-27 14:30 | Closed | Closed | 2012-03-02 13:13
2012-02-14 12:00 | 1-4712912261 | LGGC14985 | USE PO# LGGC14985 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. •Lock out / Tag out all energy sources. •Recover and weigh entire refrigerant charge using plant recovery system. •Disassemble compressor coupling. •Remove and replace compressor shaft seal. •Leak test entire chiller with nitrogen. •Evacuate chiller and perform vacuum hold test. •Check coupling alignment using laser alignment tool. •Reassemble compressor coupling. •Charge chiller with recovered refrigerant. •Furnish and install 20 gallons of new compressor oil. •Run chiller and check operation. | SLIWINSKI | 2012-02-14 12:00 | 2012-09-14 10:52 | 2012-09-14 10:52 | Closed | Closed | 2012-02-16 12:00
2012-01-22 15:17 | 1-4574444162 | LGGC14883 | DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 Job Scope: •Premium time for work performed by Mike Ianovale and Joe Fisher on Saturday 1-7-12. | SLIWINSKI | 2012-01-22 15:17 | 2012-01-23 13:34 | 2012-01-23 13:34 | Closed | Closed | 2012-01-24 15:17
2012-01-17 11:12 | 1-4544978844 | LGGC14775 | use po# LGGC14775 DuPont Experimental Station Chiller #7. •Furnish and install qty-1 new additional bursting disk relief indicators for refrigerant relief valves. •Isolate, lock out and tag out valves as required. •Disassemble assembly and clean all gasket surfaces. •Furnish and install new bursting disk and gaskets. •Leak test assembly. | SLIWINSKI | 2012-01-17 11:12 | 2012-04-30 16:03 | 2012-04-30 16:03 | Closed | Closed | 2012-01-19 11:12
2011-12-05 10:15 | 1-4311150501 | LGGC14480 | USE PO# DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 •Furnish qty-1 new seal end compressor bearing. •Furnish qty-1 new Pump end compressor bearing. •Furnish qty-1 new reverse thrust bearing. | Sliwinski | 2011-12-05 10:15 | 2011-12-14 09:08 | 2011-12-14 09:08 | Closed | Closed | 2011-12-07 10:15
2011-11-29 15:14 | 1-4276984327 | LGGC14336 | USE PO# LGGC14336 DuPont Experimental Station Chiller #7. •Furnish and install qty-5 new bursting disk relief indicators for refrigerant relief valves. oQty-2 disks on Chiller #7 Evaporator oQty-2 disks on refrigerant recovery receiver. oQty-1 disk on refrigerant recovery unit. •Isolate, lock out and tag out valves as required. •Disassemble assemblies and clean all gasket surfaces. •Furnish and install new bursting disks and gaskets. •Leak test each assembly. | SLIWINSKI | 2011-11-29 15:14 | 2012-02-06 13:21 | 2012-02-06 13:21 | Closed | Closed | 2011-12-01 15:14
2011-11-29 13:30 | 1-4276011500 | LGGC14336 | USE PO#LGGC14336 DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 Job Scope: Perform compressor bearing inspection and coupling alignment on qty-1 York OM chiller. •Lock out / Tag out chiller. •Transfer refrigerant charge to storage vessel using plant transfer system. •Disassemble compressor coupling. •Check and record compressor shaft runout and thrust readings. •Drain oil from compressor. •Dissemble compressor oil sump cover and oil pump. •Remove and inspect front compressor bearing. •Disassemble compressor shaft seal. •Remove and inspect rear compressor bearing. •Reassemble both compressor bearing assemblies with new gaskets. •Furnish and install new compressor shaft seal. •Recheck compressor runout and thrust readings. •Install new compressor oil and filters. (Supplied by customer) •Pressurize compressor with nitrogen and leak test. •Disassemble motor to gearbox coupling. •Check and record alignment of both couplings using laser tool and dial indicators. •Adjust alignments if needed to bring within factory specs. •Perform coupling maintenance. •Reassemble both couplings. •Evacuate system and perform vacuum hold test. •Recharge chiller with recovered refrigerant. •Check chiller operation. •Provide all documentation. | SLIWINSKI | 2011-11-29 13:30 | 2013-09-29 18:34 | 2013-09-29 18:34 | Closed | Closed | 2011-12-01 13:30
2011-11-29 13:24 | 1-4276011474 | LGGC14377 | USE PO# LGGC14377 DuPont Experimental Station Absorbers. #1 m/n YPCST22G46CXA s/n GLCM157836. #2 m/n YPCST22G46CXA s/n GBDM248980. #3 m/n YPCST22G46CXA s/n GADM233620. #4 m/n YPCST22G46CXA s/n GNCM9423001. Job Scope: Furnish and install new non-fragmenting type bursting disks and disk holders on each chiller. (Qty-2 per chiller. Total of qty-8). •Lock out / Tag out chiller. •Remove old carbon type disks and gaskets. •Re-fabricate piping as needed to accept new disk holders. •Furnish and install new disks and disk holders. •Pressurize and leak check around new bursting disks. •Provide all documentation. | SLIWINSKI | 2011-11-29 13:24 | 2012-04-02 14:59 | 2012-04-02 14:57 | Closed | Closed | 2011-12-01 13:24
2011-11-03 13:18 | 1-4160013757 | LGGC14145 | USE PO# LGGC14145 DuPont Experimental Station Absorber #2 m/n YPCST22G46CXA s/n GBDM248980 Job Scope: Troubleshoot low refrigerant temperature alarm. •Lock out / Tag out chiller •Check refrigerant flow to spray headers. •Change refrigerant pump. (Pump supplied by customer) •Check chiller operation. •Provide all documentation. | SLIWINSKI | 2011-11-03 13:19 | 2011-11-10 11:28 | 2011-11-10 11:28 | Closed | Closed | 2011-11-05 13:19
2011-07-13 08:51 | 1-3395663956 | LMCH10247 | Use PO# LMCH10247 DuPont Experimental Station Absorption Chillers #3 and #4 Absorber #3 m/n YPCST22G46CX s/n GADM233620 Absorber #4 m/n YPCST22G46CX s/n GNCM9423001 •Furnish and install Adva-Guard 591 chemical inhibitor for qty-2 York Absorption Chillers based on solution analysis results.. •Chiller #3…… 2.7 lbs. •Chiller #4…….2.82 lbs. | BAFFONE | 2011-07-13 08:51 | 2011-09-09 08:59 | 2011-07-29 15:11 | Closed | Closed | 2011-07-15 08:51
2011-04-14 12:17 | 1-2720351788 | LGGC10244 | Dupont Experimental Station Building 336. York YCAS190 Chiller. •Furnish and install qty-1 new condenser fan motor, fan blade, and blade mounting hardware. (Fan #7). •Furnish and install qty-1 new suction temperature sensor. •Furnish and install qty-1 new oil pressure transducer. •Start chiller and check operation. •Note: All work to be performed on a Saturday. NOT DONE | BAFFONE | 2011-04-14 12:17 | 2011-05-31 16:10 | 2011-05-31 16:10 | Closed | Closed | 2011-04-16 12:17
2011-02-16 15:55 | 1-2382254821 | LGGC8974 | Use PO # LGGC8974 DuPont Experimental Station Chiller #8. m/n OTT4G2-2BES s/n GACM117864 Furnish and install qty-1 new oil pump shaft seal kit on chiller #8. Remove and weigh refrigerant charge from chiller using plant recovery / transfer system. Disassemble oil pump and install new pump shaft seal kit. Pressurize chiller with nitrogen and leak test. Evacuate and recharge chiller with recovered refrigerant. Check oil pump operation. | BAFFONE | 2011-02-16 15:55 | 2011-02-28 12:27 | 2011-02-28 12:27 | Closed | Closed | 2011-02-18 15:55
2011-02-04 14:56 | 1-2322219561 | LGGC8619 | DuPont Experimental Station York Chiller #7. USE PO# LGGC8619 Furnish and install qty-1 new Monitech LCD display monitor on chiller control panel. Note: The Monitech display is an aftermarket display which replaces the tube only and utilizes the existing panel interface. ( No programming required). The original display is no longer available. | BAFFONE | 2011-02-04 14:56 | 2011-02-28 15:05 | 2011-02-28 15:05 | Closed | Closed | 2011-02-06 14:56
2010-12-27 08:05 | 1-2110929898 | CAROL BAFFONE | •Furnish and install qty-10 new gaskets on bursting disk relief indicators for refrigerant relief valves. •Isolate, lock out and tag out valves as required. •Disassemble assemblies and clean all gasket surfaces. •Furnish and install new gaskets. •Leak test each assembly. | BAFFONE | 2010-12-27 08:05 | 2010-12-30 10:28 | 2010-12-30 10:28 | Closed | Closed | 2010-12-29 08:05
2010-12-08 09:55 | 1-2031869374 | LGGC7651 | Provide Eddy current testing on all condenser and evaporator tubes on Chiller #7. Furnish detailed report of tube condition in hard copy and PDF format. Note: Condenser and evaporator heads must be removed and all tubes must be brush cleaned before testing can begin. (Performed by others). | BAFFONE | 2010-12-08 09:55 | 2011-01-12 12:05 | 2011-01-12 12:05 | Closed | Closed | 2010-12-10 09:55
2010-09-23 15:50 | 1-1617871854 | LDFS25135 | Furnish and install qty-1 new keypad for Absorption chiller #1. | BAFFONE | 2010-09-23 15:50 | 2010-09-27 16:43 | 2010-09-27 16:43 | Closed | Closed | 2010-09-25 15:50
2010-06-09 09:15 | 1-996861621 |  | Perform seasonal maintenance on qty-1 YCAS0190 air-cooled chiller. Clean all condenser coils with pressure washer. Change compressor oil filter. Leak check entire chiller.Perform oil and refrigerant analysis. Check all condenser fan motors and blades. Check all chiller safeties and controls. Megger test compressor motor. Check compressor starter and tighten all connections. Start chiller and check operation. Note: All work to be performed on overtime. | SLIWINSKI | 2010-06-09 09:15 | 2010-06-15 15:40 | 2010-06-15 15:40 | Closed | Closed | 2010-06-11 09:15
2010-05-26 08:45 | 1-904072214 | LGGC24TS | FINISH AND INSTALL (1) NEW LOW REFRIGERANT TEMP SWITCH. | SLIWINSKI | 2010-05-26 08:45 | 2010-06-29 13:08 | 2010-06-29 13:08 | Closed | Closed | 2010-05-28 08:45