## (2019_02_26)
Opened | SR # | Customer PO# | Type | Status | Description | Last Labor Activity | Last Material Activity | Asset # | Model # | Serial # | Date Committed | Entitlement | SR Subtype | Substatus | Billable | Contact First | Created Last Name
2019-02-25 15:55 | 1-84773414048 | 2600034674 | L&M | Scheduled | CHILLER #8 CHARGE TRANSFER & WEIGHING: DUE TO REFRIGERANT LEAKS DISCOVERED ON 01/30/2019 THE FOLLOWING WORK IS RECOMMENDED: TRANSFER ENTIRE R-134A CHARGE TO YORK CENTRAL RECOVERY TANK DOCUMENT WEIGHT OF CHARGE & CALCULATE PERCENTAGE LOSS BASED ON DESIGN TRANSFER RECOVERED CHARGE BACK INTO THE CHILLER AFTER LEAKS ARE REPAIRED (AS DECIDED BY DUPONT) DOCUMENT AMOUNT RECHARGED BACK TO CHILLER IN ORDER TO ACHIEVE A BASELINE FOR FUTURE LEAK RATE CALCULATIONS | 2019-02-22 |  | 1-FY0MJZY | OTT4G2-ZBES | GACM117864 | 2019-02-27 15:55 |  | Custom Quote | Tech Accepted | Y | Raul | Dolphin
2019-02-22 12:02 | 1-84724135703 | 6501959952 | L&M | Closed | CHILLER #10 CONDENSER WATER BOX REPAIRS - REPAIR EROSION DAMAGE DISCOVERED ON CHILLER #10'S "OUTLET END" WATERBOX GASKET CHANNEL w/ CUSTOMER SUPPLIED BELZONA 1121 "SUPER XL - METAL" REPAIR COMPOSITE | 2019-01-31 |  |  |  |  | 2019-02-24 12:02 |  | Custom Quote | Closed | Y | Raul | Dolphin
2019-02-21 13:36 | 1-84701513778 |  | L&M | Scheduled | CHILLER #8 REFRIGERANT LEAK REPAIRS (FEB. 2019) - ORDER, PICKUP, & DELIVER QTY-8 GARLOCK 3504 (G49B) 2"x 1/8"THK RING GASKETS - LOCKOUT RELIEF DEVICE 3-WAY VALVE - REMOVE ONE RUPTURE DISK AT A TIME FROM #8'S RELIEF TREE - THOROUGHLY CLEAN FLANGE FACE SURFACES & HARDWARE - INSPECT AND VERIFY RUPTURE DISK CONDITION - RE-INSTALL w/ NEW & APPROVED GASKETS & TORQUE FLANGES TO SPEC - ALL JOINTS WILL BE VERIFIED "LEAK-FREE" w/ ELECTRONIC REFRIGERANT LEAK DETECTOR AFTER INSTALLATION IS COMPLETED - REMOVE AND REPLACE LEAKING 1/2" THREADED FLARE ANGLE VALVE ON THE OIL COOLER REFRIG. VAPOR RETURN LINE. SEAL WITH APPROPRIATE REFRIG GRADE LOCTITE - FILL OUT & PROVIDE EPA REFRIGERANT LEAK REPAIR DOCUMENTATION AT THE COMPLETION OF THE JOB * FOUR Gaskets will be used in the repair and FOUR will remain with the Customer for future use * *** Refrigerant Recover and Recharge is billing billed separately to DUPONT PO#: 2600034674 / JCI SR#: 1-84627913833 *** | 2019-02-25 |  |  |  |  | 2019-02-23 13:36 |  | Custom Quote | Pending Tech Acceptance | Y | Raul | Reed
2019-02-18 14:24 | 1-84627913833 |  | L&M | In Progress | (moved to quote job 1-84773414048 ) Verify charge in Chiller #8. Remove charge and weight in the Central Recovery Tank and re-install. |  |  | 1-FY0MJZY | OTT4G2-ZBES | GACM117864 | 2019-02-20 14:26 |  | Labor & Material | Review for Completion | Y | Raul | Dolphin
2019-01-30 13:15 | 1-84255915067 | 6501959950 | L&M | Scheduled | 6501959950 CHILLER #8 ANNUAL MAINTENANCE (2019 YEAR-START) Refrigerant Leak Test chiller and Document Leaks Found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Disassemble Compressor Coupling, Clean, & Check Cold Alignment Measure & Record Compressor Low-Speed Axial Thrust Reassemble Coupling and Re-Check Compressor Cold Alignment Vacuum out Compressor Motor and Change Air Filters Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Document all tasks and Provide DuPont with a Comprehensive Report *Refrigerant & Oil Samples will be performed under a separate Quote* | 2019-02-25 |  | 1-FY0MJZY | OTT4G2-ZBES | GACM117864 | 2019-02-01 13:15 |  | Custom Quote | Tech Accepted | Y | Raul | Dolphin
2019-01-30 13:11 | 1-84255644093 | 6501959951 | L&M | Scheduled | 6501959951 CHILLER #9 ANNUAL MAINTENANCE (2019 YEAR-START) Refrigerant Leak Test chiller and Document Leaks Found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Disassemble Compressor Coupling, Clean, & Check Cold Alignment Measure & Record Compressor Low-Speed Axial Thrust Reassemble Coupling and Re-Check Compressor Cold Alignment Vacuum out Compressor Motor and Change Air Filters Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Document all tasks and Provide DuPont with a Comprehensive Report *Refrigerant & Oil Samples will be performed under a separate Quote* | 2019-02-25 |  | 1-H7K9F6K | OTT4G2-ZBES | GACM127698 | 2019-02-01 13:11 |  | Custom Quote | Tech Accepted | Y | Raul | Dolphin
2019-01-25 12:24 | 1-84160812284 | 6501960548 | L&M | Closed | CHILLER #6 EVAPORATOR TUBE PLUGGING ORDER & DELIVER Qty-1 (10-Pack) of CPI/PERMA "Pop-A-Plug" V-649-B (Brass) Tube Plugs (1,000 PSI Rated) w/ matched Precision Brushes INSTALL Tube Plugs (Qty= 2 per Tube) in the FOUR Tubes determined by Eddy-Current Analysis (performed 01/21/18 - 01/23/18) to be of a condition requiring it Tube Ends will be thoroughly cleaned, precisely honed to appropriate ID, blown out, completely dried with Nitrogen, & internally inspected via Borescope CPI/PERMA "Pop-A-Plug" V-649-B (1,000PSI Rated) Plugs will be precisely expanded into both ends of each tube A Record will be made and provided for the Customer with which Tubes were Plugged Qty-2 Plugs will be left with the Customer for future use | 2019-01-28 |  | 1-12BPQKSA | 17DA743 | 38999 | 2019-01-27 12:24 |  | Custom Quote | Closed | Y | Raul | Dolphin
2019-01-23 12:02 | 1-84110505416 | 6501952678 | L&M | Scheduled | #10 Motor Alignment. | 2019-01-23 |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2019-01-25 12:03 |  | Labor & Material | Tech Accepted | Y | Raul | Dolphin
2019-01-22 10:27 | 1-84082631601 |  | L&M | Scheduled | (SR 1-84724135703) CHILLER #10 CONDENSER WATER BOX REPAIRS |  |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2019-01-24 10:28 |  | Labor & Material | Tech Accepted | Y | Raul | Dolphin
2019-01-15 10:30 | 1-83947879493 | 6501958985 | L&M | Closed | CHILLER #10 REMOVAL, INSPECTION, & RE-INSTALLATION OF RUPTURE DISKS: - REMOVE ONE RUPTURE DISK AT A TIME FROM #10'S RELIEF TREE, FOR INSPECTION - RE-INSTALL w/ APPROPRIATE GASKETS (PROVIDED BY DUPONT) & TORQUE FLANGES TO SPEC - ALL JOINTS WILL BE VERIFIED "LEAK-FREE" w/ ELECTRONIC REFRIGERANT LEAK DETECTOR AFTER INSTALLATION IS COMPLETED * WORK WILL BE PERFORMED UNDER THE "#9 & #10 RELIEF LOCKOUT" * RUPTURE DISKS WILL BE INSPECTED BY BOTH DUPONT'S "PRESSURE RELIEF GROUP" & JCI | 2019-01-24 |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2019-01-17 10:30 |  | Custom Quote | Closed | Y | Raul | Dolphin
2019-01-14 14:02 | 1-83928082090 | 6501958985 | L&M | Closed | CHILLERS #9 & #10 RELIEF DEVICE REMOVAL, INSPECTION, & RE-INSTALLATION - LOCKOUT #9 & #10 RELIEF TREE 3-WAY VALVE (IN COORDINATION w/ DUPONT OPERATIONS) - REMOVE ONE SIDE OF #9'S RELIEF TREE (RUPTURE DISK & RELIEF VALVE) FOR INSPECTION - RE-INSTALL w/ APPROPRIATE GASKETS (PROVIDED BY DUPONT) - PREFORM THE SAME ON THE OTHER SIDE OF #9'S RELIEF TREE - REMOVE ONE RELIEF VALVE FROM #10'S RELIEF TREE (RUPTURE DISKs WERE INSPECTED IN DEC. 2018) FOR INSPECTION - RE-INSTALL w/ APPROPRIATE GASKETS (PROVIDED BY DUPONT) - PREFORM THE SAME ON THE OTHER SIDE OF #10'S RELIEF TREE - ALL JOINTS WILL BE VERIFIED "LEAK-FREE" w/ ELECTRONIC REFRIGERANT LEAK DETECTOR AFTER INSTALLATION IS COMPLETED | 2019-01-24 |  |  |  |  | 2019-01-16 14:02 |  | Custom Quote | Closed | Y | Raul | Dolphin
2019-01-08 11:56 | 1-83808360967 |  | L&M | Cancelled | (moved to quoted SR 1-83928082090) Chiller #9 AND #10: Remove ruptured disks and reliefs for inspection |  |  | 1-H7K9F6K | OTT4G2-ZBES | GACM127698 | 2019-01-10 11:59 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2018-12-28 12:37 | 1-83636066541 | 6501956331 | L&M | Closed | CHILLER #6 CONDENSER TUBE PLUGGING ORDER, PICKUP, & DELIVER Qty-1 (10-Pack) of CPI/PERMA "Pop-A-Plug" V-649-N (90/10 Cu/Ni) Tube Plugs (1,000 PSI Rated) w/ matched Precision Brushes INSTALL Tube Plugs (Qty= 2 per Tube) in the TWO Tubes determined by Eddy-Current Analysis (performed 12/17/18 - 12/20/18) Tube Ends will be thoroughly cleaned, precisely honed to appropriate ID, blown out, completely dried with Nitrogen, & internally inspected via Borescope CPI/PERMA "Pop-A-Plug" V-649-N (1,000PSI Rated) Plugs will be precisely expanded into both ends of each tube A Record will be made and provided for the Customer with which Tubes were Plugged Qty-6 Plugs will be left with the Customer for future use* * These Plugs can ONLY be used for CHILLER #6's Condenser/Sub-Cooler, because they are Copper-Nickel. All other Chiller Tubes (both Evap and Condensers) in the Powerhouse are Copper * | 2018-12-21 |  |  |  |  | 2018-12-30 12:37 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-12-27 12:35 | 1-83610966508 | 6501955455 | L&M | Closed | CHILLER #10 COMPRESSOR OIL PUMP REPLACEMENT TRANSFER ENTIRE R-134A CHARGE TO YORK CENTRAL RECOVERY TANK DOCUMENT WEIGHT OF CHARGE AND CALCULATED PERCENTAGE LOSS BASED ON DESIGN DRAIN & DISPOSE OFF THE COMPRESSOR OIL CHARGE (INTO DUPONT APPROVED WASTE OIL DRUMS) REMOVE FAULTY OIL PUMP FURNISH & INSTALL A NEW YORK OEM REPLACEMENT PUMP ENSURE ALIGNMENT OF PUMP & PIPING IS SUCH TO PREVENT EXCESSIVE STRESS FURNISH & INSTALL 10 GALLONS OF NEW YORK "J" OIL VERIFY LEAK TIGHTNESS OF PUMP, FITTINGS, & PIPE WITH A NITROGEN PRESSURE TEST VERIFY PROPER OPERATION OF PUMP BEFORE RE-INSTALLING THE REFRIGERANT CHARGE (ELECTRICAL & HYDRAULIC PERFORMANCE) EVACUATE / DEHYDRATE CHILLER & PERFORM VACUUM HOLD TEST TRANSFER RECOVERED CHARGE BACK INTO CHILLER PROVIDE DUPONT WITH EPA REFRIGERANT DOCUMENTATION | 2019-01-23 |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2018-12-29 12:35 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-12-22 14:00 | 1-83565930588 |  | L&M | Cancelled | (moving to SR 1-83636066541) Chiller #6 Condenser Tube plugging. |  |  | 1-12BPQKSA | 17DA743 | 38999 | 2018-12-24 14:01 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2018-12-18 15:26 | 1-83477191780 | 6501956333 | L&M | Closed | CHILLERS 8, 9, & 10 ANNUAL REFRIGERANT & OIL ANALYSIS (2018 YEAR-END) The following samples will be Taken, Shipped, and Analyzed by Certified Laboratories for Evaluation of Equipment Health: CHILLER #8, 9, & 10 Refrigerant CHILLER #8, 9, & 10 Compressor Oil Refrigerant & Oil Analysis Reports will be provided to DuPont with Service Recommendations (if needed). | 2018-12-26 |  |  |  |  | 2018-12-20 15:26 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-12-18 15:23 | 1-83477191310 | 6501955457 | L&M | Closed | CHILLER #7 ANNUAL REFRIGERANT & OIL ANALYSIS (2018 YEAR-END) The following samples will be Taken, Shipped, and Analyzed by Certified Laboratories for Evaluation of Equipment Health: CHILLER #7 Refrigerant CHILLER #7 Compressor Oil YORK RECOVERY TANK Refrigerant Analysis Reports will be provided to DuPont with Service Recommendations (if needed). | 2019-01-23 |  | 1-EIZYN96 | OM3000 | MRP626904 | 2018-12-20 15:23 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-12-15 00:03 | 1-83422977779 | 6501952678 | L&M | Scheduled | PO #:6501952678 Due:12/14/18 EMG Desc:Chiller #8 problems - Kevin Fraze, JCI mech was on site earlier in day and had to stay on after hours to work on this problem. Svc Hrs: NA Access:NA Contact: NA Caller:Kevin Fraze / JCI mech 302 353 0315 | 2019-02-15 |  | 1-FY0MJZY | OTT4G2-ZBES | GACM117864 | 2018-12-17 00:03 |  | Labor & Material | Scheduled After Hours | Y | Raul | Steinbach
2018-12-12 12:22 | 1-83364016333 | 6501951077 | L&M | Closed | CHILLER #6 CONDENSER EDDY CURRENT TEST (DEC 2018) EDDY-CURRENT TESTING & ANALYSIS OF ALL CONDENSER (3990), SUBCOOLER (441) TUBES *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED, BRUSHED, & VERIFIED CLEAR BEFORE TECHNICIAN ARRIVES. UNIT MUST BE READY FOR TESTING WITH NO WAITING TIME.* **THIS WORK WILL NEED TO BE SCHEDULED IN ADVANCE TO GUARANTEE AVAILABILITY OF TECHNICIAN. ACCESS TO SITE AND POWERHOUSE WILL NEED TO BE ARRANGED & PROVIDED FOR THE TECHNICIAN BY DUPONT** | 2018-12-27 |  | 1-12BPQKSA | 17DA743 | 38999 | 2018-12-14 12:22 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-12-12 12:14 | 1-83364431437 | 6501951077 | L&M | Closed | CHILLER #6 EVAPORATOR EDDY CURRENT TEST (JAN 2019) EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR (2586) *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED, BRUSHED, & VERIFIED CLEAR BEFORE TECHNICIAN ARRIVES. UNIT MUST BE READY FOR TESTING WITH NO WAITING TIME.* **THIS WORK WILL NEED TO BE SCHEDULED IN ADVANCE TO GUARANTEE AVAILABILITY OF TECHNICIAN. ACCESS TO SITE AND POWERHOUSE WILL NEED TO BE ARRANGED & PROVIDED FOR THE TECHNICIAN BY DUPONT** | 2019-01-28 |  | 1-12BPQKSA | 17DA743 | 38999 | 2018-12-14 12:15 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-12-10 10:55 | 1-83312748537 |  | L&M | Cancelled | (moved to two different jobs- 1-83364431437 and 1-83364016333 )CHILLER #6 EDDY-CURRENT (2018-2019) EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR (2586), CONDENSER (3990), SUBCOOLER (441) TUBES (7017 TOTAL) FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED TO DUPONT UPON COMPLETION. *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED, BRUSHED, & VERIFIED CLEAR BEFORE TECHNICIAN ARRIVES. UNIT MUST BE READY FOR TESTING WITH NO WAITING TIME.* **THIS WORK WILL NEED TO BE SCHEDULED IN ADVANCE TO GUARANTEE AVAILABILITY OF TECHNICIAN. ACCESS TO SITE AND POWERHOUSE WILL NEED TO BE ARRANGED & PROVIDED FOR THE TECHNICIAN BY DUPONT** | [5 empty] | 2018-12-12 10:55 |  | Custom Quote | Customer Cancelled | Y | Raul | Reed
2018-12-06 14:29 | 1-83254615109 | Approver: R. Cozza | L&M | Closed | CHILLER #10 ANNUAL MAINTENANCE (2018 YEAR-END) Refrigerant Leak Test chiller and Document Leaks Found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Disassemble Compressor Coupling, Clean, & Check Cold Alignment Measure & Record Compressor Low-Speed Axial Thrust Reassemble Coupling and Re-Check Compressor Cold Alignment Vacuum out Compressor Motor and Change Air Filters Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Document all tasks and Provide DuPont with a Comprehensive Report *Refrigerant & Oil Samples will be performed under a separate Quote* | 2019-01-31 |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2018-12-08 14:29 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-10-31 14:36 | 1-81044975607 | 6501900202 | L&M | Closed | 2018 ABSORBER SERVICE & SUPPORT: Absorber Seasonal Startup Work Performed Outside of the Contract Maintenance Agreement, due to Delays & Issues with the New Cooling Tower. NTE- $6000 Original Quote ID#: 1-W0GJ44F | 2018-10-31 |  |  |  |  | 2018-11-02 14:36 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-10-31 14:23 | 1-81042969595 | Cozza | L&M | Closed | LABOR/MATERIAL INVOLVED IN RESEARCH/TESTING ABSORBER REFRIGERANT (H20) TREATMENT - | 2018-10-31 |  |  |  |  | 2018-11-02 14:23 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-10-31 14:20 | 1-81042621797 | COZZA | L&M | Closed | RENTAL OF QTY-2 DE-IONIZING TANKS FOR 2 WEEKS - Cost of QTY-2 "Mixed-Bed" De-Ionizing Tank Rentals (QTY-2 weeks), intended to create on-site DI Water for the original Ammonia Removal Project (JCI Quote#: 1-Z91E3GO) - Cost includes Initial Pickup/Delivery from Vendor in Philadelphia and Final Return/Delivery back to Vendor in Philadelphia | 2018-10-31 |  |  |  |  | 2018-11-02 14:20 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-10-25 13:14 | 1-80764101843 |  | L&M | Closed | ABSORBER #1 LABOR / MATERIAL UTILIZED ON 10/24/2018 **The price of this quote is to cover the labor involved in responding to a service call on 10/24, regarding tripped solution pump overloads in ABS#1** - Situation was investigated. - Main Solution Pump (P1) Overload was replaced with on-site spare (JCI's) - Secondary Spray Pump (P2) Overload was replaced with on-site spare (JCI's) - Absorber Operation is back to Normal **Quoted price also includes cost to replace both on-site spare Overloads** | 2018-10-31 |  |  |  |  | 2018-10-27 13:14 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-10-02 13:44 | 1-79161835257 | Cozza | L&M | Closed | ABS #3: Labor to install Steam Regulator Parts. | 2018-10-16 |  |  |  |  | 2018-10-04 13:45 |  | Labor & Material | Closed | Y | Raul | Dolphin
2018-10-01 06:00 | 1-77976295122 |  | PSA | Closed | Preventive Maintenance | 2018-11-14 |  |  |  |  | 2018-09-27 07:34 | 1-ZKX15VZ | Scheduled Service | Closed | N | Raul | Administrator
2018-09-27 15:47 | 1-78240491883 | 6501927190 | L&M | Closed | Additional Labor to install 4,000 lbs of refrigerant to York Central Recovery Tank. | 2018-09-27 |  |  |  |  | 2018-09-29 15:48 |  | Labor & Material | Closed | Y | Raul | Dolphin
2018-09-27 07:26 | 1-78138940797 |  | L&M | Cancelled | (moved) RESEARCH AMMONIA REMOVAL FROM ABSORBERS. | [5 empty] | 2018-09-29 07:27 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2018-09-24 12:51 | 1-77873988838 | 6501927190 | L&M | Closed | DIAGNOSTICS & REPLACEMENT OF ABS#3's MAIN SOLUTION PUMP MOTOR OVERLOADS ** This quote covers the expense of Labor & Material immediately required & provided 8/29/18 ** The failure occurred during the initial test run of the newly installed Refrig Pump Motor, while running close to full load. As per design, this initiates an immediate shutdown / lockout of the entire Absorber (All Pumps & Steam) preventing the Dilution Cycle required for a safe shutdown. Operators & Electricians were notified. Both fuses in the MCC bucket were blown. Power was locked out, the failed overload assembly (an original) was removed, and replaced with a new spare from truck stock. Verified the P1 Motor was electrically sound (Normal and Balanced resistance between all phases & > 550 meg ohm resistance from phase to ground). Checked all wiring and components in the the YORK Main Power Panel (Physically & Electrically). No issues were found. The electricians installed new 60A fuses in the MCC bucket and re-applied power. The controls & pumps were tested. Supply Voltage & Motor Currents were all in within Operational Norms. It was then restarted & ran until intentionally taken offline, 8Hr later, without issue. - FURNISH QTY-1 New Overload Assembly for the Main Solution Pump (P1) - REMOVE & REPLACE the Failed Component - INSPECT Motor Windings, Controls, & Wiring for Shorts, Damage, or other Anomalies - ENSURE Proper Operation of Absorber - INFORM Powerhouse Staff of Findings & Repairs Made | 2018-09-24 |  |  |  |  | 2018-09-26 12:51 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-09-21 14:50 | 1-77266890935 | 6501927190 | L&M | Closed | Absorber #3 Steam Regulator Trouble shooting and Service. | 2018-09-21 |  |  |  |  | 2018-09-23 14:52 |  | Labor & Material | Closed | Y | Raul | Dolphin
2018-09-21 14:47 | 1-77266890688 | 6501927189 | L&M | Closed | ABSORBER #3 FISHER STEAM REGULATOR REPAIR PARTS: - FURNISH QTY-2 Main Diaphragms - FURNISH QTY-2 Gaskets - FURNISH QTY-1 Pilot Regulator - EXPEDITED SHIPPING ** Quote does not include labor costs to install ** | 2018-09-28 |  |  |  |  | 2018-09-23 14:47 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-09-20 07:27 | 1-76955883072 |  | L&M | Cancelled | (moved to SR's 1-81042621797 and 1-81042969595) AMMONIA REMOVAL - ABSORBERS #1 - 4 - Rental and Delivery of Qty- 2 Mixed-Bed De-Ionizing Tanks, for on-site DI Water creation - Each Absorber will be ran individually, Refrigerant generated, Removed, and either Stored or Disposed of. (DuPont will be responsible for Disposal, if the water cannot be put in the process sewer. Waste Refrigerant will have an approximate PH of 10 and Ammonia level between 100-150 ppm) - The Absorber will then be refilled with the same quantity of pure DI water, Ran, Solution Diluted, Refrigerant Re-Generated, Ammonia Level Checked, and Process Repeated as necessary to Reduce Ammonia content down to an acceptable Level - This Process will be performed on all Absorbers #1 - #4 - All equipment and temporary storage drums will be removed from powerhouse after process is completed - Lithium Bromide Samples will be taken and sent to Lab for analysis at the completion of each Absorber's Ammonia Removal Process. (This will be the Final Sample for the season, and will be covered under the Maintenance Contract) | [5 empty] | 2018-09-22 07:27 |  | Custom Quote | Created In Error | Y | Raul | Dolphin
2018-08-30 15:45 | 1-75572824951 |  | L&M | Cancelled | (to SR 1-77873988838) ABS 3 MAIN SOLUTION PUMP MOTOR OVERLOAD ISSUE. |  |  | GADM233620 | YPC ST 22G | GADM233620 | 2018-09-01 15:47 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2018-08-29 13:54 | 1-75405778459 | 6501916931 | L&M | Closed | QUOTE: 1-XIE6F08 PO: 6501916931 SR: 1-75405778459 ABSORBERS #1 - #4 INHIBITOR QUOTE (JULY 2018) PROVIDE MATERIAL: LITHIUM MOLYBDATE & NITRATE INHIBITORS based on recent Solution Analysis to bring Levels back to Optimal. * The necessary amount of inhibitor was already added to the Absorbers on 07/27/18. This quote is for replenishing what was used of the on-site inhibitor supply. * | 2018-09-24 |  |  |  |  | 2018-08-31 13:54 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-08-29 13:46 | 1-75405052078 | 6501916911 | L&M | Closed | QUOTE: 1-XJSY4T8 PO: 6501916911 SR: 1-75405052078 CHILLERS #8,9,10 YORK J OIL STOCK REPLENISHMENT (30 GALLONS) - FURNISH, DELIVER, & CONSOLIDATE 30 GALLONS of New YORK J (for use when needed by CHILLERS #8,9,10) - There is currently no "J" Oil left in the Powerhouse. Immediate resupply is recommended. | 2018-09-06 |  |  |  |  | 2018-08-31 13:46 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-08-01 06:00 | 1-69586568664 |  | PSA | Closed | Preventive Maintenance | 2018-10-16 |  |  |  |  | 2018-07-03 07:47 | 1-PALS0R5 | Scheduled Service | Closed | N | Raul | Administrator
2018-07-25 13:53 | 1-70721879041 | 6501906836 | L&M | Closed | 6501906836 ABSORBER #3 REFRIGERANT PUMP SPINDLE VALVE & REPLACEMENT SUPPORT - Furnish & Deliver Qty-1 New 1/2" Spindle Valve to Replace the Original Valve, due to Corrosion Damage - Removal and Installation will be performed by a DuPont Approved contractor, under the guidance of Johnson Controls and in accordance with YORK Factory Specifications for Absorber Welding - Assistance will be provided by Johnson Controls, as needed. (i.e. Instruction, Supervision, Nitrogen Purging, Final Leak Test Verification, etc.) | 2018-08-24 |  | GADM233620 | YPC ST 22G | GADM233620 | 2018-07-27 13:53 |  | Custom Quote | Closed | Y | Raul | Reed
2018-07-11 10:29 | 1-70195442164 | 6501901448 | L&M | Closed | 6501901448 ABSORBER #3 REFRIG. PUMP MOTOR REPLACEMENT LOCKOUT / TAGOUT ABS#3 in coordination w/ DuPont Operations Isolate Refrigerant Pump (P3) by means of Suction & Discharge Valves Introduce Nitrogen Pressure into Pump Casing, and Ensure that Valves Hold * Safely Remove and Store any Refrigerant remaining in the Pump Casing Disassemble and Remove the Motor/Pump Assembly Inspect & Clean the Pump Volute Remove and Replace the Volute Impeller Wearing Ring Removed and Inspect the Impeller from the old Motor/Pump Assembly ** Furnish New Pump Motor Install Impeller on New Motor, and Verify Radial & Axial Clearances Install New Motor/Pump Assembly into Pump Volute Casing with new Gasket Pressurize Casing with Nitrogen and Ensure No Leaks Evacuate Casing and Perform Vacuum Hold Test Open Pump Isolation Valves Rewire Refrig. Pump Motor Unlock Absorber, Test Run, Document Pump Pressures and Amperages Return Absorber to Normal Service * If Isolation Valves do not hold, the entire Absorber Vacuum will need to be broken with Nitrogen, and re-evacuated at the completion of the motor replacement. This extra work will NOT be cover by this quote * ** If the impeller requires machining or re-balancing, this will be performed at an additional cost ** | 2018-08-31 |  |  |  |  | 2018-07-13 10:29 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-07-11 07:55 | 1-70191928421 | 6501896708 | L&M | Closed | YORK CENTRAL RECOVERY UNIT & LIQUID LINE RELIEF RETROFIT SERVICE & SUPPORT Perform Lockout of RECOVERY UNIT & LIQUID REFRIG. LINE in Coordination with DuPont Recover Refrigerant from Unit & Line into External Cylinders Verify Unit & Line are Depressurized & Purged with Nitrogen Disassemble & Remove the Rupture Disk & Relief Valve from the Unit and the Relief Valve from the Line, allowing MDAVIS to proceed with Piping Modifications and Installation of the Relief Header All Piping & Installation of Piping; Rupture Disks, and Relief Valves for the Recovery Unit & Line shall be Provided by MDAVIS and/or DuPont Installation of the New Rupture Disk w/ appropriate Gaskets/Fasteners will be performed by JCI (Appropriate Torque will be Determined, Set & Documented) *All Piping must be in place and within specs for Misalignment, previous to Disk Installation* Recovery Unit & Line will be Pressurized with Nitrogen All new Refrigerant Connections will be Tested Any Leaks discovered on the piping installed by the MDAVIS, will be their responsibility to repair After Piping & Relief Devices are Verified Leak Free, Nitrogen Pressure will be Safely Vented Outdoors Recovery Unit & Line will then be Evacuated, followed by a Vacuum Hold Test The Recovered Refrigerant will be Transfered back into the Unit & Line The Recovery Unit's Oil will be Changed, with DuPont supplied YORK "K" EPA Refrigerant Documentation will be Provided at the Completion of the Project | 2018-09-28 |  |  |  |  | 2018-09-14 19:41 |  | Custom Quote | Closed | Y | Chris | Dolphin
2018-07-11 07:36 | 1-70191656731 | 6501900198 | L&M | Closed | 6501900198 ABSORBER #2: FURNISH & REPLACE Defective MicroPanel Keypad Discovered on 06/28/2018 | 2018-08-09 |  | GBDM248980 | YPC ST 22G | GBDM248980 | 2018-07-13 07:36 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-07-03 16:05 | 1-69778277082 | 6501895641 | L&M | Closed | 1-VPUQHGP quote 6501895641 YORK CENTRAL RECOVERY TANK REFRIG. ACCESS VALVES - FURNISH & INSTALL QTY-3 INDUSTRIAL REFRIGERATION GRADE ACCESS VALVES (While Tank is Still Decommissioned) VALVE LOCATIONS: 1] 3/4" LIQUID SAMPLE LINE (BOTTOM of TANK) 2] 3/4" "DIRT LEG" PIPE (BOTTOM of TANK) 3] 3/4" VAPOR ACCESS (TOP of TANK) | 2018-09-18 |  |  |  |  | 2018-07-05 16:05 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-07-01 06:00 | 1-67539505783 |  | PSA | Closed | Preventive Maintenance | 2018-07-31 |  |  |  |  | 2018-06-03 09:03 | 1-PALS0R5 | Scheduled Service | Closed | N | Raul | Administrator
2018-06-30 00:13 | 1-69531626381 | Cozza | L&M | Closed | Due:6/29/18 Desc:Absorber 3 refrigerant pump motor failure. Manual solution dilution was required. Customer needed additional OT support and service for absorbers. Svc Hrs:24/7 Access:None Contact:Raul Cozza (302) 695-7842 Caller:Kevin Fraze (302) 353-0315 | 2018-08-30 | [6 empty] | Labor & Material | Closed | Y | Raul | Landers
2018-06-29 13:13 | 1-69503459104 | 6501898128 | L&M | Closed | ABSORBER #3 DIGITAL INPUT BOARD UPGRADE - Remove & Replace the original Digital Input Board (c.1993) with the latest revision, due to incompatibility with the new MicroBoard (Main Logic Board) just installed. - Replacement is necessary in order to make the Absorber operational. - An added feature of the new Digital Input Board is the ability to run a "Limited Dilution Cycle" on Generator Power, if a Power Outage and subsequent Loss of Water Flow happened to occur during Absorber Operation. (Whenever power is lost while an Absorber is running, and it is not restored quickly to allow the Solution Pumps to perform a Dilution Cycle, the likelihood of Crystallization is very high) | 2018-06-28 |  |  |  |  | 2018-07-01 13:13 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-06-21 06:47 | 1-69173645344 | 6501900202 | L&M | Cancelled | Absorber Seasonal Startup Work Performed Outside of the Contract Maintenance Agreement, due to Delays & Issues with the New Cooling Tower | [5 empty] | 2018-06-23 06:55 |  | Labor & Material | Customer Cancelled | Y | Raul | Fraze
2018-06-13 16:18 | 1-68738559155 |  | L&M | Closed | REPAIR OF REFRIGERANT LEAKS COMING FROM Aux. refrigerant angle vavle on top of YORK Central recovery tank. | 2018-08-07 |  |  |  |  | 2018-06-15 16:20 |  | Labor & Material | Closed | Y | Raul | Dolphin
2018-06-13 10:07 | 1-68728578445 | 6501866668 | L&M | Closed | 65018666668 Chiller 10 Leak repair (2018) Repair of the following Leak found on 3/23/2018: 3/8 Copper Flare on oil-return line. REPAIRS REMAINING TO BE COMPLETED WHEN CUSTOMER WILL SHUT DOWN/LOCK OUT CHILLER: REPAIR OF THE FOLLOWING LEAKS FOUND ON 03/23/2018: OIL COOLER THERMOSTATIC VALVE O-RING SEAL 2" HOT GAS VALVE O-RING SEALS GASKETS ON BOTH RUPTURE DISKS HIGH SPEED THRUST COVER PLATE O-RING SEAL | 2018-06-07 |  |  |  |  | 2018-06-15 10:07 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-06-11 13:18 | 1-68690100490 | 6501891530 | L&M | Closed | 6501891530 ABSORBER #3 MICROBOARD REPLACEMENT - Remove & Replace the defective main Logic Board - Install latest YORK Paraflow Software Revision (EPROM) - Install New Battery Backup RTC Chip - Restore all previous Program Setpoints - Perform Steam Valve Calibration - Verify proper operation of MicroBoard, including Remote Communication with Powerhouse Automation System | 2018-06-25 |  | GADM233620 | YPC ST 22G | GADM233620 | 2018-06-13 13:18 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-06-11 13:15 | 1-68690100273 | 6501891532 | L&M | Closed | 6501891532 ABSORBER #3 ABSOLUTE PRESSURE GAUGE REPLACEMENT ** Last year the Vacuum Gauge used to measure Purge Tank and Absorber Shell Absolute Pressures was found to be Inaccurate and was Removed ** - FURNISH & INSTALL a New Dial-Type Absolute Pressure Gauge (0-40 mmHgA Range) - VERIFY Accuracy of Gauge | 2018-06-28 |  |  |  |  | 2018-06-13 13:15 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-06-06 10:20 | 1-68541236461 |  | L&M | Cancelled | (moved to SR 1-58805089790) RUSH ORDER - REFRIGERATION GASKETS PER BOB KING: RELATED TO: YORK CENTRAL RECOVERY TANK RELIEF RETROFIT SERVICE & SUPPORT | [5 empty] | 2018-06-08 10:21 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2018-06-04 08:39 | 1-68224567482 | 6501895197 | L&M | Closed | Arctic Chillers E306 and E309- both are having issues per Carol Baffone (302) 218-9737. | 2018-06-15 |  |  |  |  | 2018-06-06 08:42 |  | Labor & Material | Closed | Y | CAROL | Dolphin
2018-06-01 15:43 | 1-67602431865 | 6501821002 | L&M | Closed | - CHILLER #7 SERVICE: HIGH GEARBOX OIL DIFFERENTIAL PRESSURE AND LOW SUPPLY PRESSURE ALARMS. - CHILLERS #8/#9/#10 LOW COMPRESSOR OIL LEVELS. ADD CUSTOMER SUPPLIED OIL. | 2018-09-19 |  |  |  |  | 2018-06-03 15:44 |  | Labor & Material | Closed | Y | Raul | Dolphin
2018-06-01 06:00 | 1-65245048091 |  | PSA | Closed | Preventive Maintenance See SR 1-63738398676 | 2018-09-21 |  |  |  |  | 2018-05-03 10:02 | 1-PALS0R5 | Scheduled Service | Closed | N | Raul | Administrator
2018-05-25 15:08 | 1-66708811126 | 6501887272 | L&M | Closed | 6501887272 SUVA R-134A - 4,000LBS - DELIVERED and INSTALLED INTO the YORK CENTRAL RECOVERY TANK to REPLENISH ON-HAND STOCK for FUTURE USE in YORK CENTRIFUGALS | 2018-09-27 |  |  |  |  | 2018-05-27 15:08 |  | Custom Quote | Closed | Y | Raul | Reed
2018-05-01 06:00 | 1-63738398676 |  | PSA | Closed | Preventive Maintenance | 2018-07-06 |  |  |  |  | 2018-04-03 11:07 | 1-PALS0R5 | Scheduled Service | Closed | N | Raul | Administrator
2018-04-26 13:14 | 1-64665980108 | 6501876572 | L&M | Closed | 6501876572 YORK Central Recovery Liquid Line Leak Repair: - Lockout/Tagout of all refrigerant lines connected to the common liquid recovery line - Pressurize line with nitrogen and verify the location of the leak - Purge line of nitrogen and perform an official Line Break, demonstrating isolation and depressurization of the line to be repaired - Label the section of corroded & leaking 1-1/4" piping needing to be removed and replaced - Prep and assist MDAVIS, as needed, with this work - Perform official pneumatic pressure test of liquid line with nitrogen per ASME B31.3 & DuPont requirements. Verify all joints are leak free. Record & provide DuPont with documentation of test - Evacuate liquid line and perform a vacuum hold test - Flush line out with liquid refrigerant from Chiller #7. Run refrigerant through filter-driers, into Central Tank, and then transfer back to #7 - Remove Lockout/Tagout from all refrigerant valves when work is completed | 2018-04-30 |  |  |  |  | 2018-04-28 13:14 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-04-23 10:13 | 1-64484582517 | 6501873610 | L&M | Closed | 6501873610 4/20/2018 YORK CENTRAL RECOVERY TANK RUPTURE DISK REMOVAL Per Customer Request: Isolate & Remove One of the Two Rupture Disks on the Central Recovery Tank Adjust Piping and Connect the Two Flanges together (which previously held the Rupture Disk) such that Tank Pressure will be on the Relief Valve Inlet at all times Evacuate line between Isolation Valve and Relief Valve Open Isolation Valve and Verify no refrigerant leaks on the line or through the Relief Valve Leave this line open and close the isolation valve for the other Rupture Disk Provide documentation of change to DuPont | 2018-04-27 |  |  |  |  | 2018-04-25 10:13 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-04-23 07:56 | 1-64480139762 |  | L&M | Cancelled | (moved to sr 1-64484582517) Urgent Ruptured Disk Removal.. | [5 empty] | 2018-04-25 07:57 |  | Labor & Material | Created In Error | Y | Raul | Dolphin
2018-04-02 14:41 | 1-63764006724 |  | L&M | Cancelled | (moved to quoted job 1-64665980108) YORK Central Recovery System Liquid Line Repairs. | [5 empty] | 2018-04-24 14:42 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2018-03-30 09:35 | 1-63695549302 | 6501866668 | L&M | Closed | 6501866668 CHILLER #10 REFRIGERANT LEAK REPAIRS (2018): DUE TO REFRIGERANT LEAKS DISCOVERED ON 03/23/2018 THE FOLLOWING WORK IS RECOMMENDED: TRANSFER ENTIRE R-134A CHARGE TO YORK CENTRAL RECOVERY TANK DOCUMENT WEIGHT OF CHARGE AND CALCULATED PERCENTAGE LOSS BASED ON DESIGN REPAIR OF THE FOLLOWING LEAKS FOUND ON 03/23/2018: OIL COOLER THERMOSTATIC VALVE O-RING SEAL 2" HOT GAS VALVE O-RING SEALS GASKETS ON BOTH RUPTURE DISKS HIGH SPEED THRUST COVER PLATE O-RING SEAL 3/8 COPPER FLARE ON OIL-RETURN LINE VERIFY LEAK TIGHTNESS WITH NITROGEN PRESSURE TEST EVACUATE / DEHYDRATE CHILLER & PERFORM VACUUM HOLD TEST TRANSFER RECOVERED CHARGE BACK INTO CHILLER PROVIDE DUPONT WITH EPA DOCUMENTATION | 2018-12-19 |  |  |  |  | 2018-04-01 09:35 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-03-28 14:39 | 1-63565108321 | 6501864525 | L&M | Closed | 6501864525 CHILLER #7 OIL SEPARATOR REPAIRS & COMMISSIONING Isolate Oil Separator Repair Refrigerant Leaks Discovered on 1-1/4 Flange and Two Sightglasses Leak Test, Evacuate, Recommission. Replacement of Blown Insertion Heater Fuses Multiple Additions of Oil to Maintain Proper Compressor Sump Level (through the duration of Oil Separator being Offline) Multiple Removals of Oil to Maintain Proper Compressor Sump Level (once Oil Separator was back Online and properly returning Oil to Sump) | 2018-03-30 |  |  |  |  | 2018-03-30 14:39 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-03-22 15:24 | 1-63380036421 | 6501862720 | L&M | Closed | 6501862720 CHILLER #7 YORK K OIL STOCK REPLENISHMENT (40 GALLONS) - FURNISH, DELIVER, & CONSOLIDATE 40 GALLONS of New YORK K (for use when needed by CHILLER #7) | 2018-03-28 |  |  |  |  | 2018-03-24 15:24 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-03-19 15:26 | 1-62653596356 |  | L&M | Cancelled | (moved to SR 1-62653596356) #9 Motor alignment adjustment | 2018-03-19 |  |  |  |  | 2018-03-21 15:28 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2018-02-28 09:41 | 1-61766516449 | 6501785366 | L&M | Closed | CHILLER #8 (ADDITIONAL WORK PERFORMED): ASSISTING DuPont Personnel with CHILLER MOTOR ALIGNMENT TROUBLESHOOTING & ASSISTING DuPont Electricians with MOTOR STARTER ISSUES on Day of Startup ADDING YORK J Compressor Oil to CHILLERS #9 & #10 due to Low Levels (Oil Provided By DuPont) EMPTYING Seal Oil Bottles on CHILLERS #9 & #10 and Recording Quantities for Yearly Leakage Rate Calculation | 2018-02-27 |  |  |  |  | 2018-03-02 09:41 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-02-23 15:27 | 1-61586979721 |  | L&M | Cancelled | (to sr 1-63565108321) #7 Oil Recovery Ruptured disk/relief replacement, leak repairs and recommissioning. |  |  | 1-EIZYN96 | OM3000 | MRP626904 | 2018-02-25 15:29 |  | Labor & Material | Created In Error | Y | Raul | Dolphin
2018-02-23 09:40 | 1-61576546733 | 6501785366 | L&M | Closed | DESICCANT AIR BREATHER ADAPTERS FURNISH QTY - 3 HYDRAULIC ADAPTERS (1-1/4" NPT x 1-1/2"-16 UNF) | [5 empty] | 2018-02-25 09:40 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-02-21 10:02 | 1-61523605002 | 6501778777 | L&M | Closed | ​Responded to Service Call regarding Low Compressor Oil Level in CHILLER #7. | 2018-03-19 |  | 1-EIZYN96 | OM3000 | MRP626904 | 2018-02-23 10:03 |  | Labor & Material | Closed | Y | Raul | Dolphin
2018-02-09 15:17 | 1-61334960562 |  | L&M | Cancelled | ( to sr 1-61576546733 - something odd happed to the quote-to-sr process) JCI to Supply Pipe adapters for Chiller Desiccant air breathers | [5 empty] | 2018-02-11 15:18 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2018-01-26 10:44 | 1-60524830267 |  | L&M | Cancelled | (moved to sr 1-61766516449) Chiller #8: Assist DuPont with Motor Alignment. | [5 empty] | 2018-01-28 10:45 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2018-01-26 10:35 | 1-60524494687 |  | L&M | Cancelled | (moved to another sr)- quoted job Chiller #10: Low compressor oil level- add oil. | [5 empty] | 2018-01-28 10:41 |  | Labor & Material | Created In Error | Y | Raul | Dolphin
2018-01-25 15:01 | 1-60507439543 | 6501853388 | L&M | Closed | Chiller #9 Annual Maintenance (JAN 2018) Refrigerant Leak Test chiller and Document Leaks Found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Disassemble Compressor Coupling, Clean, & Check Cold Alignment Measure & Record Compressor Low-Speed Axial Thrust Reassemble Coupling and Re-Check Compressor Cold Alignment Vacuum out Compressor Motor and Change Air Filters Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Document all tasks and Provide DuPont with a Comprehensive Report *Refrigerant & Oil Samples will be performed under a separate Quote* | 2018-03-26 |  |  |  |  | 2018-01-27 15:02 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-01-25 14:59 | 1-60506490261 | 6501861449 | L&M | Closed | Chiller #10 Annual Maintenance (MARCH. 2018) Refrigerant Leak Test chiller and Document Leaks Found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Disassemble Compressor Coupling, Clean, & Check Cold Alignment Measure & Record Compressor Low-Speed Axial Thrust Reassemble Coupling and Re-Check Compressor Cold Alignment Vacuum out Compressor Motor and Change Air Filters Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Document all tasks and Provide DuPont with a Comprehensive Report *Refrigerant & Oil Samples will be performed under a separate Quote* | 2018-03-28 |  |  |  |  | 2018-01-27 14:59 |  | Custom Quote | Closed | Y | Raul | Dolphin
2018-01-09 10:07 | 1-60202627249 | 6501833534 | L&M | Closed | 6501833534 CHILLERS #8, #9, #10 PRESSURE TRANDSDUCER SPARES FURNISH the Following YORK Parts to have on hand for CHILLERS #8, #9, #10: QTY-5: HIGH PRESSURE TRANSDUCERS (P/N#: 025-28678-001) QTY-5: LOW PRESSURE TRANSDUCERS (P/N#: 025-28678-104) | [5 empty] | 2018-01-11 10:07 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-12-29 14:57 | 1-59981980005 | 6501817598 | L&M | Closed | 6501817598 Chiller #7 annual maintenance (2017 year-end part 1). Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible). Furnish and install compressor oil filters, and all refrig filter-driers. Furnish 10 gallons of new York "k" oil to replenish quantities removed from vessels during maintenance. Disassemble motor coupling, clean, measure/record cold alignment. Disassemble compressor coupling and clean. Assist DuPonts instrumentation techs with the removal, calibration, & reinstallation of chillers pressure transducers & RTD temp sensors. | 2017-12-28 |  |  |  |  | 2017-12-31 14:57 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-12-28 15:52 | 1-59931287174 | 6501821002 | L&M | Closed | CHILLER #7 OIL SUMP TOP SIGHTGLASS: - PROACTIVE Replacement of TOP Oil Sump Sight-Glass. * The TOP Sight-Glass was Replaced while the Oil Sump was Empty and Pressure was Absent from Chiller * * Both TOP & BOTTOM Sight-Glasses were Originally Planned to be Replaced, but only QTY-1 was available in STOCK at the Time of Purchase. However, due to additional stock becoming available much sooner than expected and the Compressor Oil Charge still being externally stored, the 2ND (TOP) Glass was also Replaced* ** This quote simply covers the added cost of the Sight-Glass and Labor to Change. The Transfer of Oil TO and FROM the temporary drum, and the cost of the Bottom Sight-Glass and Labor to Replace has been covered under QUOTE # 1-R0IFJSX ** | 2017-12-27 |  |  |  |  | 2017-12-30 15:52 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-12-26 10:06 | 1-59866440572 |  | L&M | Closed | CHILLER #7 RELIEF PROJECT GASKETS | 2017-12-28 |  |  |  |  | 2017-12-28 10:06 |  | Custom Quote | Closed | Y | Chris | Dolphin
2017-12-13 15:31 | 1-58806996905 | 6501821002 | L&M | Closed | 6501821002 CHILLER #7 OIL SUMP SIGHTGLASS REPLACEMENT TRANSFER current Compressor Oil Charge into Clean Drum FURNISH & REPLACE Bottom Oil Sump SIGHTGLASS (Due to Hairline Cracks) REINSTALL Compressor Oil Charge | 2017-12-14 |  |  |  |  | 2017-12-15 15:31 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-12-13 14:15 | 1-58805089790 | 6501825667 | L&M | Closed | 6501825667 YORK CENTRAL RECOVERY TANK RELIEF RETROFIT SERVICE & SUPPORT Perform Lockout of YORK RECOV TANK in Coordination with DuPont Transfer any Remaining Charge from TANK to YORK CHILLERS & Document Verify TANK is Depressurized & Purged with "House" Nitrogen Disassemble & Remove the Two 2" Rupture Disks, allowing for MDAVIS to proceed with Piping Modifications and Installation of the New Relief Header All Piping & Installation of Piping; Rupture Disks, Relief Valves, and 3-Way Valve for the TANK shall be Provided by MDAVIS and/or DuPont Installation of the Two New Rupture Disks w/ appropriate Gaskets/Fasteners will be performed by Johnson Controls (Appropriate Torque will be Determined, Set & Documented) *All interconnecting Piping must be in place and within specs for Misalignment / Strain, previous to Disk Installation* After all Relief Work is Complete, the TANK will be Pressurized with Nitrogen All new Refrigerant Connections will be Tested Any Leaks discovered on the piping installed by the MDAVIS, will be their responsibility to repair After Piping & Relief Devices are Verified Leak Free, Nitrogen Pressure will be Safely Vented Outdoors Entire TANK will then be Evacuated, followed by a Vacuum Hold Test (Verifying Tightness and Dryness of TANK) Refrigerant Gas Charge will be Transfered back into the TANK EPA Refrigerant Documentation will be Provided | 2018-09-18 |  |  |  |  | 2017-12-15 14:16 |  | Custom Quote | Closed | Y | Chris | Dolphin
2017-12-01 10:27 | 1-58589405354 | 6501823103 | L&M | Closed | CHILLER #8 REFRIGERANT LEAK REPAIRS (DEC. 2017) TRANSFER R-134A CHARGE TO YORK CENTRAL RECOVERY TANK DOCUMENT WEIGHT OF CHARGE & CALCULATED PERCENTAGE LOSS BASED ON DESIGN REPAIR OF THE FOLLOWING REFRIGERANT LEAK FOUND ON 11/27/17: COMPRESSOR PRE-ROTATION VANE SHAFT SEAL DISSMANTLE & REMOVE OLD SEAL ASSEMBLY FURNISH & INSTALL NEW SEAL ASSEMBLY WITH NEW ORINGS, GASKET, & FASTENERS PROPERLY SET & TORQUE SEAL 12" FREE-COOLING BUTTERFLY O-RING FLANGE SEALS RIG, DISSMANTLE, & REMOVE VALVE CLEAN VALVE & FLANGE SURFACES INSTALL NEW O-RING SEALS IN VALVE FLANGE FACES RE-INSTALL VALVE & PROPERLY TORQUE FLANGES *(Does not include any additional repairs to valve if discovered & necessary upon removal) COMPRESSOR OIL RESERVOIR ACCESS COVER GASKET REMOVE ACCESS COVER & OLD GASKET CLEAN COMPRESSOR & COVER SURFACES INSPECT RESERVOIR INSTALL NEW GASKET RE-INSTALL ACCESS COVER & PROPERLY TORQUE VERIFY TIGHTNESS OF ALL REPAIRS WITH NITROGEN PRESSURE TEST PERFORM EVACUATION/DEHYDRATION, & VACUUM HOLD TEST TRANSFER RECOVERED CHARGE BACK INTO CHILLER PROVIDE DUPONT WITH EPA LEAK REPAIR DOCUMENTATION | 2017-12-20 |  | 1-FY0MJZY | OTT4G2-ZBES | GACM117864 | 2017-12-03 10:27 |  | Custom Quote | Closed | Y | Raul | Reed
2017-11-29 16:15 | 1-58329012419 | 6501812408 | L&M | Closed | CH #7 Relief Retrofit Service & Support: Part 1 Meet with Customer, Prepare for job, Recover refrigerant and put on a nitrogen holding blanket. Customer will determine when Part 2 of the job will continue. (Original quote 1-QFC14IN for $8,101.75. Part 1 will invoice in the amount of $3,857.48. Part 2 will invoice in the amount of $4,244.27) | 2017-11-17 |  |  |  |  | 2017-12-01 16:15 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-11-22 15:14 | 1-58055227604 | 6501817598 | L&M | Closed | (6501817598) CHILLER #7 ANNUAL MAINTENANCE (2017 YEAR-END Part 2) FURNISH and INSTALL Gearbox Oil Filters and Oil (*Gear/Motor Oil furnished by DuPont*) INSPECT Gears and Internal Gearbox Components REPACK Motor Coupling with Grease and REASSEMBLE MEASURE/RECORD Compressor Axial Thrust & Coupling Cold Alignment, REASSEMBLE Coupling VACUUM out Compressor Motor BRUSH CLEAN all Oil Cooler Tubes (Gear & Compressor) REMOVE & PERFORM Annual Maintenance on COMPRESSOR CAPACITY CONTROL VANE ACTUATOR DOCUMENT all Tasks and Provide DuPont with a Comprehensive Report | 2018-01-30 |  |  |  |  | 2017-11-24 15:14 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-11-20 10:48 | 1-57994324284 | 6501816123 | L&M | Closed | Chiller #8 Annual Maintenance (2017 YEAR-END) Refrigerant Leak Test chiller and Document Leaks Found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Disassemble Compressor Coupling, Clean, & Check Cold Alignment Measure & Record Compressor Low-Speed Axial Thrust Reassemble Coupling and Re-Check Compressor Cold Alignment Vacuum out Compressor Motor and Change Air Filters Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Document all tasks and Provide DuPont with a Comprehensive Report *Refrigerant & Oil Samples will be performed under a separate Quote* | 2017-12-20 |  |  |  |  | 2017-11-22 10:48 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-11-16 13:32 | 1-57931332938 | 6501817650 | L&M | Closed | 6501817650 CHILLERS 8, 9, & 10 ANNUAL REFRIGERANT & OIL ANALYSIS The following samples will be Taken, Shipped, and Analyzed by Certified Laboratories for Evaluation of Equipment Health: CHILLER #8, 9, & 10 Refrigerant CHILLER #8, 9, & 10 Compressor Oil Refrigerant & Oil Analysis Reports will be provided to DuPont with any Service Recommendations (if needed). | 2017-11-21 |  |  |  |  | 2017-11-18 13:32 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-11-10 10:36 | 1-57829091567 | 6501812408 | L&M | Closed | CHILLER #7 RELIEF RETROFIT SERVICE & SUPPORT Perform Lockout of CHILLER #7 in Coordination with DuPont Transfer Chiller Charge to Central Recovery Tank per EPA Regs & Record Weight Verify all Sections of Chiller are Depressurized & Purged with "House" Nitrogen Disassemble & Remove the Two 2" Evaporator Rupture Disks, allowing for the Assigned Mechanical Contractor to proceed with Piping Modifications and Installation of the New Relief Header All Piping & Installation of Piping; Rupture Disks, Relief Valves, and 3-Way Valve for the Evaporator shall be Provided by the Assigned Contractor and/or DuPont Installation of the Two New Rupture Disks w/ appropriate Gaskets/Fasteners will be performed by Johnson Controls (Appropriate Torque will be Determined, Set & Documented) *All interconnecting Piping must be in place and within specs for Misalignment / Strain, previous to Disk Installation* After all Relief Work is Complete, the Chiller will be Pressurized with Nitrogen All new Refrigerant Connections will be Tested Any Leaks discovered on the piping installed by the Mechanical Contractor, will be their responsibility to repair After Piping & Relief Devices are Verified Leak Free, Nitrogen Pressure will be Safely Vented Outdoors Entire Chiller will then be Evacuated, followed by a Vacuum Hold Test (Verifying Tightness and Dryness of System) Refrigerant Charge will be Transfered back into the Chiller EPA Refrigerant Documentation will be Provided | 2018-01-26 |  |  |  |  | 2017-11-12 10:36 |  | Custom Quote | Closed | Y | Chris | Dolphin
2017-11-10 10:15 | 1-57828978548 | 6501817588 | L&M | Closed | CHILLER #7 ANNUAL REFRIGERANT & OIL ANALYSIS The following samples will be Taken, Shipped, and Analyzed by Certified Laboratories for Evaluation of Equipment Health: CHILLER #7 Refrigerant CHILLER #7 Compressor Oil CHILLER #7 Gearbox Oil YORK RECOVERY TANK Refrigerant Analysis Reports will be provided to DuPont with any Service Recommendations (if needed). | 2017-11-10 |  |  |  |  | 2017-11-12 10:15 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-11-01 13:17 | 1-57575415130 | 6501807345 | L&M | Closed | E306 RTP CHILLER AUTO AIR VENT REPLACEMENT & MISC. SERVICE - Furnish Qty-1 B&G Series 78 Auto Air Vent - Removal and Replacement of Faulty Spirax/Sarco Air Vent on Air Separator - Replacement of 1/4" Ball Valve and Copper Line on Low Side of Andover Controls' Differential Pressure Transmitter (The above work has already been performed and completed) | 2017-10-19 |  |  |  |  | 2017-11-03 13:17 |  | Custom Quote | Closed | Y | CAROL | Dolphin
2017-10-12 11:29 | 1-57125113604 | 6501807345 | L&M | Closed | E306 RTP CHILLER PUMP#2 - Due to the loss of system glycol and the failure of PUMP#1's Shaft Seal, proactive replacement of PUMP#2's seal is suggested, while system is empty. - Furnish Qty-1 Armstrong Mechanical Seal Kit and Qty-1 Volute Gasket. - Disconnect Wiring on Pump Motor. - Assist DuPont's Pump Team, as needed, in the Removal and Replacement of Seal. - Rewire Pump Motor, Start and Check Operation. * This Quote is Priced such that the DuPont Pump Team will be performing the seal replacement in their shop * | 2017-10-13 |  |  |  |  | 2017-10-14 11:29 |  | Custom Quote | Closed | Y | PAUL | Dolphin
2017-10-12 11:27 | 1-57125113325 | 6501807345 | L&M | Closed | E306 RTP YORK CHILLER MODEL: YCAL0046EE SERIAL: 11531K65368876 - Shutdown and Lock-Out YORK RTP CHILLER according to DuPont & JCI's Safety Requirements. - Depressurize Chilled Glycol Loop, by temporarily draining water/glycol mixture into, empty drums (provided by DuPont. - Remove current "Paddle" Style Flow Switch in YORK Chiller. - Furnish & Install Premium "Thermal" Style Flow Switch: (Stainless Steel Insertion Probe, Remote-Mounted Control Monitor /w Adjustable Relay Output, & Interconnecting Cable) - Furnish & Install necessary pipe fittings for Probe Installation. - Install any necessary Wiring and Conduit. - Make wiring adjustments to Chiller. - Re-Install Glycol with Appropriate amount of Water to attain System Design Concentration of 30%. - Bleed Air from System, using Automatic Vents. - Un-Lock and Restart System, Check for Leaks, Adjust Flow-Switch Settings and Verify Operation. - Prove DuPont with all necessary Documentation. Premium Flow Switch is capable of Sensing flows from 0.083 Ft/Sec (2 GPM)* to 9.83 Ft/Sec (226 GPM)* * Flow rates based on specified velocities through 3" steel pipe | 2017-10-17 |  |  |  |  | 2017-10-14 11:27 |  | Custom Quote | Closed | Y | PAUL | Dolphin
2017-10-10 15:36 | 1-57088158569 |  | L&M | Cancelled | (to sr 1-57575415130) Replacement of Spirax/Sarco Air Vent on Chilled Water Air separator |  |  | 11531K65368876 | YCAL0046EE46XEB/R410A | 11531K65368876 | 2017-10-12 15:38 |  | Labor & Material | Customer Cancelled | Y | PAUL | Dolphin
2017-10-10 12:46 | 1-57084202094 |  | L&M | Closed | (8K709046 10/17 claim complete-requires review and approval.) Paul stated E306 RTP is experiencing no chilled water system pressure and glycol on the floor. | 2017-10-12 |  | 11531K65368876 | YCAL0046EE46XEB/R410A | 11531K65368876 | 2017-10-12 12:48 |  | Warranty to Equipment | Closed | N | PAUL | Dolphin
2017-10-01 06:00 | 1-55109527850 |  | PSA | Closed | Preventive Maintenance | 2017-10-31 |  |  |  |  | 2017-09-03 14:02 | 1-PALS0R5 | Scheduled Service | Closed | N | Raul | Administrator
2017-09-14 08:55 | 1-55330460961 | 6501785361 | L&M | Closed | CHILLER #10 Leaving Chilled Water Temp Sensor and Damaged Cable: - Remove and Replace Damaged Cable from the MicroPanel to the Leaving Chilled Water Temp Sensor. - Remove and Replace Leaving Chilled Water Temp Sensor. - Check Calibration and Accuracy of Sensor. ** This quote also covers the time already spent diagnosing and making temporary repairs on 08/21/17. ** | 2017-09-15 |  |  |  |  | 2017-09-16 08:55 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-09-05 16:12 | 1-55165238982 | 6501785365 | L&M | Closed | 6501785365 ABSORBERS #1 - #4 PROVIDE MATERIAL: LITHIUM MOLYBDATE INHIBITOR based on recent Solution Analysis to bring Levels back to Optimal. * The necessary amount of inhibitor was already added to the Absorbers on 08/25/17, due to Customer request for Early Shutdown. This quote is for replenishing what was used of the on-site inhibitor supply. * | 2017-09-13 |  |  |  |  | 2017-09-07 16:13 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-09-05 16:00 | 1-55164988394 | 6501785366 | L&M | Closed | 6501785366 Standby chiller support 09/05/2017. | 2017-09-05 |  |  |  |  | 2017-09-07 16:01 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-08-31 12:41 | 1-55066190528 | 6501785366 | L&M | Closed | 8/26 Overtime requested by the customer to perform end of season maintenance early due to closure of one of the cooling towers. DuPont Master agreement Labor Rate is $151.20 per hour. 9 hrs x $75.60 = $680.40 | 2017-08-26 |  |  |  |  | 2017-09-02 12:41 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-08-25 15:43 | 1-54747390862 |  | L&M | Cancelled | (TIME MOVED TO PSA) End of Season maintenance, including inhibitor. | 2017-08-26 |  |  |  |  | 2017-08-27 15:44 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2017-08-21 11:12 | 1-54630793558 |  | L&M | Cancelled | (TO SR 1-55330460961) Chiller #10: Faulty Leaving Chilled Water Temp Sensor and Damaged sensor cable. | [5 empty] | 2017-08-23 11:13 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2017-08-18 13:06 | 1-54597712254 |  | L&M | Closed | Abs #3, Refrigerant Pump Motor replacement (with customer supplied part) | 2017-08-25 |  |  |  |  | 2017-08-20 13:07 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-08-16 15:39 | 1-54556841145 | 6501773542 | L&M | Closed | RUSH ON ABSORBER END OF SEASON SAMPLES: - Extra costs involved for a Laboratory RUSH (24-48hr) on 4 Lithium Bromide Samples. - Extra cost for Expedited Shipping to Laboratory. **(These extra costs are outside the scope of the Contract, and were requested by the Customer, due to End of Season Absorber Shutdown being moved ahead by 1 month)** | 2017-08-25 |  |  |  |  | 2017-08-18 15:39 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-08-15 15:51 | 1-54517796786 | 6501778019 | L&M | Closed | ABSORBER #1 PURGE PUMP MOTOR STARTER & TRANSDUCER Furnish & Install New Overload Block w/Aux Contact & Motor Contactor for Purge Pump Motor Furnish & Install New Purge Pump Pressure Transducer | 2017-08-31 |  |  |  |  | 2017-08-17 15:51 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-08-15 12:40 | 1-54505335665 | 6501778777 | L&M | Closed | 6501778777 Trouble shoot ABS #3 Pump issues and check for signs of crystallization | 2017-08-31 |  | GADM233620 | YPC ST 22G | GADM233620 | 2017-08-17 12:47 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-08-15 08:16 | 1-54486496905 | 6501778010 | L&M | Closed | 6501778010 CHILLER #9 BLOWN CONTROL FUSE (DIAGNOSTICS & REPAIRS: - CHILLER #9's had shutdown Friday 8/11/17, blowing the 120V YORK Control Panel Fuse 2 times in a row. - This quote includes the labor involved in responding to and troubleshooting the issue. - Discovered Oil Return Line Solenoid Coil shorted to ground. - Disconnected and Isolated Coil Wiring. - Will furnish new Solenoid Coil, wiring, and electrical interconnects. - Will Test Functionality & Ensure Proper Operation, Voltage & Current. - Will Assist in Restarting Chiller. | 2017-08-28 |  |  |  |  | 2017-08-17 08:16 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-08-14 14:13 | 1-54424901203 | 6501778018 | L&M | Closed | CHILLERS #8, #9, #10: - FURNISH 20 Gallons of YORK "J" OIL to Replenish Powerhouse Supply for the YORK OT Chillers. - Four 5-Gallon Pales will be delivered to the Powerhouse and stored with the rest of the Chiller Oil Supply. | 2017-08-14 |  |  |  |  | 2017-08-16 14:13 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-08-14 12:21 | 1-54417211679 |  | L&M | Cancelled | (TO SR 1-54486496905 ) Powerhouse Chiller #9, Blew fuse on Friday. | [5 empty] | 2017-08-16 12:24 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2017-08-07 13:35 | 1-53745308445 | 6501773542 | L&M | Closed | 6501773542 Assist with the Re-start of Chiller #7, after shutdown. Add oil to compressor - check operation. | 2017-08-07 |  |  |  |  | 2017-08-09 13:42 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-08-04 15:22 | 1-53714943616 | 6501773542 | L&M | Closed | 6501773542 Add compressor and motor oil to chillers #8, 9 and 10. Oil is customer supplied. | 2017-08-18 |  |  |  |  | 2017-08-06 15:24 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-08-04 15:18 | 1-53714943404 | 6501773542 | L&M | Closed | 6501773542 Re-locate solution filter canister to Abs. #2, Install new filters and begin filtering. | 2017-08-21 |  |  |  |  | 2017-08-06 15:20 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-08-03 10:52 | 1-53649606061 | 6501773542 | L&M | Closed | 6501773542 Reconfigure Chillers #8,9, and 10- Microgateway per Jerry Carney | 2017-08-03 |  |  |  |  | 2017-08-05 10:57 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-08-02 20:19 | 1-53494663790 | 6501773542 | L&M | Closed | 6501773542 Due:2-Aug Desc:Performed manual dilution on absorbers #2and #3. Svc Hrs:N/A Access:N/A Contact:Raul Cozza 302-892-5766 Caller:Kevin Fraze 302-353-0315 | 2017-08-02 | [6 empty] | Labor & Material | Closed | Y | Raul | Watkins
2017-08-01 06:00 | 1-51949088924 |  | PSA | Closed | Preventive Maintenance | 2017-08-28 |  |  |  |  | 2017-07-03 12:15 | 1-HAKE4G3 | Scheduled Service | Closed | N | Raul | Administrator
2017-07-11 08:52 | 1-52089702219 |  | L&M | Cancelled | (Moved to SR 1-51949088924) Paul Barns FISEN WARRANTY. Problem: Cause: Solution: ???? | 2017-07-13 |  | 11531K65368876 | YCAL0046EE46XEB/R410A | 11531K65368876 | 2017-07-13 08:53 |  | Warranty to Equipment | Created In Error | N | PAUL | Dolphin
2017-07-01 06:00 | 1-50899520998 |  | PSA | Closed | Preventive Maintenance | 2017-08-04 |  |  |  |  | 2017-06-03 07:51 | 1-HAKE4G3 | Scheduled Service | Closed | N | Raul | Administrator
2017-06-29 10:19 | 1-51838395351 | 6501740662 | L&M | Closed | #7: Repairs to Conoflow Actuator | 2017-06-06 |  |  |  |  | 2017-07-01 10:19 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-06-26 13:57 | 1-51694527366 | 6501757668 | L&M | Closed | 6501757668 ABSORBER SOLUTION FILTERS Due to HIGH CONCENTRATION of SUSPENDED SOLIDS after the STARTUP of ABSORBER #1, FILTERING was REQUIRED 2 SETS of FILTERS were REPLACED while ABS#1 was in OPERATION. (Labor will be cover by this Quote) FURNISH 24 New PALL Bromide Solution FILTERS to REPLENISH onsite Supply (6 Filters per Changeout) REMOVE and REPLACE current clogged Filters on ABSORBER #1 CLEAN out Canister EVACUATE and RETURN to Service | 2017-07-31 |  |  |  |  | 2017-06-28 13:57 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-06-22 09:14 | 1-51626193941 |  | L&M | Cancelled | (moving to quote 1-NPVTNXZ) Absorber #1 Purge Pump Motor Starter Replacement. | [5 empty] | 2017-06-24 09:15 |  | Labor & Material | Customer Cancelled | Y | PAUL | Dolphin
2017-06-22 08:53 | 1-51625745587 | 6501757664 | L&M | Closed | ABSORBERS #1 - #4 PROVIDE MATERIAL: LITHIUM MOLYBDATE & NITRATE INHIBITORS based on recent Solution Analysis to bring Levels back to Optimal. *Included in the price of this quote, is the 1LB of LITHIUM NITRATE proactively added to ABSORBER #1 at startup, due to concerns of internal corrosion.* | 2017-06-22 |  |  |  |  | 2017-06-24 08:53 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-06-22 08:49 | 1-51625507272 | 6501757663 | L&M | Closed | ABSORBER #3: Furnish & Replace Faulty MicroPanel Keypad Discovered on Startup | 2017-06-23 |  |  |  |  | 2017-06-24 08:49 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-06-01 06:00 | 1-49400587467 |  | PSA | Closed | Preventive Maintenance | 2017-06-27 |  |  |  |  | 2017-05-03 07:53 | 1-HAKE4G3 | Scheduled Service | Closed | N | Raul | Administrator
2017-05-17 12:35 | 1-49844903353 |  | L&M | Cancelled | ( moved to SR 1-51838395351) #7 CONOFLOW Actuator Service and Material order | [5 empty] | 2017-05-19 12:36 |  | Labor & Material | Created In Error | Y | Raul | Dolphin
2017-05-08 16:34 | 1-49598628764 | 6501738598 | L&M | Closed | ABSORBER #2: FURNISH Qty-2 CONDENSATE FLOW CONTROL VALVES, (to be Installed by MDAVIS) Properly ADJUST Valves to Design Flows during the Startup of the Absorber **Old Valves should be Saved as Emergency Spares** | 2017-05-30 |  |  |  |  | 2017-05-10 16:34 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-05-01 06:00 | 1-48472723228 |  | PSA | Closed | Preventive Maintenance- SERVICE SCHEDULED IN MAY- CUSTOMER REQUEST TO PULL AHEAD. Due to repairs - the SSV work could not be done in May. | 2017-05-26 |  |  |  |  | 2017-05-01 13:03 | 1-HAKE4G3 | Scheduled Service | Closed | N | Raul | Administrator
2017-04-26 07:56 | 1-48965085254 | 6501733954 | L&M | Closed | ABSORBER #1 RUPTURE DISK INSPECTION & REPLACEMENT Perform LOCK-OUT per DuPont & JCI Requirements ENSURE Vessel is Completely Depressurized DISMANTLE BOTTOM Rupture Disk Companion Flanges & REMOVE OSECO Rupture Disk Assembly DISASSEMBLE OSECO (PRDI) Holder, Exposing (PLR) Disk REMOVE Blown Rupture Disk and Hand over to DuPont Personnel for Investigation INSPECT Condition and thoroughly CLEAN 6" Companion Flanges Re-Install OSECO Holder w/ NEW Disk (Provided by DuPont) & Appropriate Ring Gaskets. Properly TORQUE companion Flanges to OSECO's specifications PRESSURIZE ABSORBER Vessel with Nitrogen Pressure and R-134a Trace Gas LEAK TEST Rupture Disks with both Electronic Detector & Soap Bubbles APPLY a thin coat of Vacuum Sealant around Disk Holder Gasket & Flange to Increase certainty of Air Molecule Seal Provide DuPont with any DOCUMENTATION requested ***Any scaffolding necessary to perform work safely will be provided by DuPont*** | 2017-05-15 |  | GLCM157836 | YPC ST 22G | GLCM157836 | 2017-04-28 07:56 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-04-20 11:50 | 1-48814192110 | 6501730675 | L&M | Closed | 6501730675 CHILLER #7 LEAK REPAIR REPAIR REFRIGERANT LEAKS FOUND ON 04/17/17: [1] Refrig. Sample Valve, Bottom of Evaporator [2] 1/2" Pipe Thread in Compressor Discharge Line for Transducer [3] Threaded Well in Compressor Discharge Line for RTD [4] Drain Valves on Bottom of Comp. Volutes [5] 1/4" Threaded 45L for Balance Piston Transducer Assist DuPont Instrumentation Technician with Removal of Transducers for Calibration Pressurize Chiller with Nitrogen and verify Leak Free Evacuate Chiller & Perform Vacuum Hold Test **Chiller Re-Charge is covered under JCI Quote#: 1-LP24C0S** | 2017-05-30 |  | 1-EIZYN96 | OM3000 | MRP626904 | 2017-04-22 11:50 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-04-20 09:42 | 1-48811045116 | 6501731064 | L&M | Closed | 6501731064 ABSORBER #1 HIGH PRESSURE SAFETY CUTOUT SWITCH During the Seasonal Shutdown, when Absorber #1 was Pressurized with Nitrogen, it was discovered that the High Pressure Cutout Switch was not Opening. Upon further investigation the switch was found to be Defective. SCOPE: FURNISH Qty-1 YORK Approved First Stage Generator High Pressure Cutout LOCK-OUT ABSORBER #1 as needed INSTALL New Switch ADJUST & VERFIY Cutout Setting VERIFY Installation is LEAK-FREE ***This work will need to be performed prior to Seasonal Purge and Start-Up work, due to Safety Switch being Non-Isolatable*** | 2017-04-28 |  |  |  |  | 2017-04-22 09:42 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-04-13 15:53 | 1-48708552989 | 6501715797 | L&M | Closed | CHILLER #9 CONDENSER TUBE PLUGGING FURNISH & INSTALL Tube Plugs (Qty= 2 per Tube) in the THREE Condenser Tubes determined by Eddy-Current Analysis to be Restricted with a portion of the tube Unverifiable Tubes Ends will be thoroughly cleaned, precisely honed to appropriate ID, & blown out / completely dried with Nitrogen CPI/PERMA "Pop-A-Plug" V-649-B (1,000PSI Rated) Plugs will be precisely expanded into both ends of restricted tube A Record will be made and provided for DuPont with which Tubes were Plugged This quote also includes the cost of the precision steel honing brushes used to perform the work | 2017-03-17 |  |  |  |  | 2017-04-15 15:53 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-03-17 14:30 | 1-48130592782 | 6501729020 | L&M | Closed | CHILLER #7 ANNUAL MAINTENANCE (2017) REMOVE REFRIGERANT SAMPLE / Send to Lab for CHEMICAL ANALYSIS REFRIGERANT LEAK TEST Chiller and Document Leaks found (repair minor leaks, if possible) TRANSFER R134A Charge to Storage Tank & Record Total Weight (Leaving 5psi on Chiller) FURNISH and INSTALL Compressor Oil Filters, and ALL REFRIG FILTERDRIERS FURNISH and INSTALL Gearbox Oil Filters and Oil (*Gear/Motor Oil furnished by DuPont*) INSPECT Gears and Internal Gearbox Components DISASSEMBLE Motor Coupling, CLEAN, MEASURE/RECORD Cold Alignment REPACK Motor Coupling with Grease and REASSEMBLE DISASSEMBLE Compressor Coupling and CLEAN MEASURE/RECORD Compressor Axial Thrust & Coupling cold Alignment, REASSEMBLE Coupling VACUUM out Compressor Motor BRUSH CLEAN all Oil Cooler Tubes (Gear & Compressor) TRANSFER R134A Charge back into Chiller & RECORD Quantity of Transfer DOCUMENT all Tasks and Provide DuPont with a Comprehensive Report | 2017-05-31 |  |  |  |  | 2017-03-19 14:30 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-03-16 14:54 | 1-48107179309 | 6501717034 | L&M | Closed | 6501717034 REMOVAL & REPLACEMENT OF ALL ABSORBER RUPTURE DISKS (QTY8) In accordance with DuPont's Vessel Relief Device PM Program, both (Qty2) OSECO Rupture Disks on ABSORBERS #1#4 shall be REMOVED and REPLACED with NEW disks (PROVIDED BY DUPONT) SCOPE PER ABSORBER (Performed ONE at a Time): Perform LOCKOUT per DuPont & JCI Requirements Safely RELEASE Nitrogen Blanket from ABSORBER & Ensure Vessel is Completely Depressurized DISMANTLE Rupture Disk Companion Flanges & REMOVE OSECO Rupture Disk Assemblies DISASSEMBLE OSECO (PRDI) Holders, Exposing (PLR) Disk INSPECT Condition of OLD Disks and Holders (Note any Damage Observed) If Disk Holders are in GOOD Condition, thoroughly CLEAN as per OSECO specs, INSTALL NEW Disks (PROVIDED BY DUPONT) into Holders INSPECT Condition and thoroughly CLEAN 6" Companion Flanges ReInstall OSECO Holders w/ NEW Disks, Appropriate Ring Gaskets, & NEW Flange Bolts Properly TORQUE companion Flanges to OSECO's specifications PRESSURIZE ABSORBER Vessel with Nitrogen Pressure and R134a Trace Gas LEAK TEST Rupture Disks with both Electronic Detector & Soap Bubbles Safely RELEASE Nitrogen & reduced Absorber pressure below atmospheric with vacuum pump APPLY a thin coat of Vacuum Sealant around Disk Holder Gasket & Flange to Increase certainty of Air Molecule Seal Provide DuPont with any DOCUMENTATION requested ***Any scaffolding necessary to perform work safely will be provided by DuPont*** | 2017-03-31 |  |  |  |  | 2017-03-18 14:54 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-03-16 10:22 | 1-48098644929 | 6501697258 | L&M | Closed | CHILLER #10 EVAPORATOR WATERBOX REPAIRS: CLEAN AND PREPARE WATERBOX HEAD FOR STEEL EPOXY COATING APPLY BELZONA 1121 "SUPER XLMETAL" (PURCHASED UNDER DUPONT PO#: 6501690015) TO FILL IN PITS AND GOUGING CLEAN UP AND ENSURE EPOXY INTEGRITY AFTER 24HR CURE TIME SHAPE HARDENED EPOXY AS NEEDED PAINT ANY BARE STEEL INSTALL REPAIRED DIVISION PLATE WITH NEW CHANNEL GASKETS & SEAL WITH CAULK | 2017-03-13 |  |  |  |  | 2017-03-18 10:22 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-03-16 01:42 | 1-48094330627 |  | L&M | Cancelled | CHILLER #7 ANNUAL MAINTENANCE (2017) |  |  | 1-EIZYN96 | OM3000 | MRP626904 | 2017-03-18 01:45 |  | Labor & Material | Customer Cancelled | Y | Raul | Fraze
2017-03-13 09:09 | 1-48030927221 |  | L&M | Cancelled | CHILLER #10 EVAPORATOR WATERBOX REPAIRS |  |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2017-03-15 09:10 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2017-03-08 15:16 | 1-47954372704 | 6501713698 | L&M | Closed | (6501713698) CHILLER #10 PRV SHAFT SEAL REPLACEMENT REPAIR OF THE FOLLOWING REFRIGERANT LEAK FOUND ON 03/03/17: COMPRESSOR PREROTATION VANE SHAFT SEAL DISMANTLE & REMOVE OLD SEAL ASSEMBLY FURNISH & INSTALL NEW SEAL ASSEMBLY WITH NEW ORINGS, GASKET, & FASTENERS PROPERLY SET & TORQUE SEAL VERIFY TIGHTNESS WITH NITROGEN PRESSURE TEST ***COST OF REFRIGERANT RECOVERY & RECHARGING IS COVERED UNDER DUPONT PO#: 6501711947*** ***EVACUATION / DEHYDRATION WILL BE COVERED UNDER JCI QUOTE# 1M0XUGZP*** | 2017-03-10 |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2017-03-10 15:16 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-03-08 15:05 | 1-47953222455 | 6501713695 | L&M | Closed | (6501713695) CHILLER #10 REFRIGERANT PIPING LEAK REPAIR: REPAIR OF THE FOLLOWING LEAKS FOUND ON 03/03/17: 1-1/2" THREADED LIQUID REFRIGERANT TEE FEEDING OIL COOLER COMP. OIL RESERVOIR EQUALIZING LINE 1/4 THREADED FLARE ELBOW CUT & DISMANTLE REFRIGERANT LIQUID FEED PIPING & FITTINGS HAND THREAD 1/2" STEEL PIPING INSTALL NEW 1-1/2" THREADED TEE, BUSHINGS, STEEL FLARE ADAPTERS, & 3/4"OD FLARED STEEL TUBING VERIFY LEAK TIGHTNESS WITH NITROGEN PRESSURE TEST EVACUATE/ DEHYDRATE CHILLER & PERFORM VACUUM HOLD TEST ***COST OF REFRIGERANT RECOVERY & RECHARGING IS COVERED UNDER DUPONT PO#: 6501711947*** | 2017-03-22 |  |  |  |  | 2017-03-10 15:05 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-03-06 07:55 | 1-47874641859 | 6501716828 | L&M | Closed | (6501716828) E306 RTP Chilled Water Loop: Calculate appropriate System Fill Pressure based on height of highest coil and specific gravity of the Chilled Water Isolate/Drain Expansion Tank Increase Expansion Tank Bladder Pressure to System Fill Pressure with Nitrogen and Document Set Glycol Feeder to System Fill Pressure and Engage Manually Run Chilled Water Pumps in YORK RTP Chiller at various speeds with all Air Vents open Increase Water Temperature as needed (w/assistance of DuPont) to facilitate air removal Monitor process When all air is removed, isolate airvents required by DuPont, and reopen Expansion Tank to System Train and Provide Literature as needed to DuPont Personnel | 2017-03-24 |  |  |  |  | 2017-03-08 07:55 |  | Custom Quote | Closed | Y | PAUL | Dolphin
2017-03-06 07:48 | 1-47873229676 | 6501711947 | L&M | Closed | (6501711947) CHILLER #10: Due to Refrigerant Leaks discovered on 03/03/2017 the following work is Recommended: Transfer entire R134A charge to YORK Central Recovery Tank Document weight of charge and calculated percentage loss based on design Provide DuPont with documentation Transfer recovered charge back into the Chiller after Leak Repair or DuPont's declining to repair | 2017-03-14 |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2017-03-08 07:48 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-02-28 13:15 | 1-47444087633 | sr cancelled | L&M | Closed | (6501715797) CHILLER #9 Condenser Tube Plugging |  |  | 1-H7K9F6K | OTT4G2-ZBES | GACM127698 | 2017-03-02 13:16 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-02-28 12:52 | 1-47443336030 | 6501709952 | L&M | Closed | (6501709952) Chiller #10 Annual Maintenance 2017 Remove Refrigerant Sample for Chemical Analysis Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return FilterDrier Furnish & Install SightGlass in Oil Return Line Change Compressor Oil w/ YORK J (Provided by DuPont) *IF REQUIRED* Disassemble Compressor Coupling and Check Cold Alignment Check LowSpeed Compressor Axial Thrust Reading Reassemble Coupling and ReCheck Compressor Coupling Cold Alignment Vacuum out Compressor Motor and Change Air Filters Change Oil in Compressor Motor Bearings (Provided by DuPont) Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Documents all tasks and Provide Comprehensive Report to DuPont | 2017-03-16 |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2017-03-02 12:52 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-02-28 10:22 | 1-47436369564 | 6501697258 | L&M | Closed | (6501697258) CHILLER #9 EVAPORATOR WATERBOX REPAIRS: CLEAN AND PREPARE TUBE SHEET DIVISION PLATE TRACKING FOR STEEL EPOXY COATING APPLY BELZONA 1121 "SUPER XLMETAL" (PURCHASED UNDER DUPONT PO#: 6501690015) TO FILL IN PITS AND GOUGING CLEAN UP AND ENSURE EPOXY INTEGRITY AFTER 24HR CURE TIME SHAPE HARDENED EPOXY AS NEEDED PAINT ANY BARE STEEL ASSIST MDAVIS WITH INSTALLATION AND GASKETING OF REPAIRED DIVISION PLATE | 2017-03-16 |  |  |  |  | 2017-03-02 10:22 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-02-27 12:08 | 1-47405246199 |  | L&M | Cancelled | (temporary holding spot for #9 Waterbox repair under PO 6501697258 NEED QUOTE) | [5 empty] | 2017-03-01 12:09 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2017-02-27 11:57 | 1-47402231723 | 6501690015 | L&M | Closed | (EMERG. PO 6501690015) Order Goodway Brushes for tube cleaning. | 2017-02-27 |  |  |  |  | 2017-03-01 12:02 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-02-13 16:01 | 1-46720117811 | 6501701543 | L&M | Closed | 6501701543 CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4.975ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: TRANSFER REFRIGERANT CHARGE INTO CENTRAL RECOVERY TANK DOWN TO EPA SPECS BRING UP TO ATMOSPHERIC PRESSURE WITH SITE NITROGEN REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, O-RINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING EVACUATE CHILLER AND PERFORM VACUUM HOLD TEST TRANSFER REFRIGERANT CHARGE BACK INTO CHILLER | 2017-02-28 |  | 1-H7K9F6K | OTT4G2-ZBES | GACM127698 | 2017-02-15 16:01 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-02-13 15:55 | 1-46718363513 |  | L&M | Cancelled | CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4975ml/hr This is double the factory recommended max leak rate of 223ml/hr (signal point for replacement) SCOPE: TRANSFER REFRIGERANT CHARGE INTO CENTRAL RECOVERY TANK DOWN TO EPA SPECS BRING UP TO ATMOSPHERIC PRESSURE WITH SITE NITROGEN REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, ORINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING EVACUATE CHILLER AND PERFORM VACUUM HOLD TEST TRANSFER REFRIGERANT CHARGE BACK INTO CHILLER | [5 empty] | 2017-02-15 15:55 |  | Custom Quote | Customer Cancelled | Y | Raul | Dolphin
2017-02-13 15:45 | 1-46719052659 |  | L&M | Cancelled | CHILLER #9 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#9 seal oil leak has been calculated at 4975ml/hr This is double the factory recommended max leak rate of 223ml/hr (signal point for replacement) SCOPE: TRANSFER REFRIGERANT CHARGE INTO CENTRAL RECOVERY TANK DOWN TO EPA SPECS BRING UP TO ATMOSPHERIC PRESSURE WITH SITE NITROGEN REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, ORINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING EVACUATE CHILLER AND PERFORM VACUUM HOLD TEST TRANSFER REFRIGERANT CHARGE BACK INTO CHILLER | [5 empty] | 2017-02-15 15:45 |  | Custom Quote | Customer Cancelled | Y | Raul | Dolphin
2017-02-10 20:07 | 1-46674736377 | 6501700807 | L&M | Closed | CHILLER # 7 OIL STOCK REPLENISHMENT: FURNISH QTY-6 5gal Pales of YORK "K" (30 Total Gallons) | 2017-02-15 |  |  |  |  | 2017-02-12 20:07 |  | Custom Quote | Closed | Y | Raul | Reed
2017-02-10 11:56 | 1-46661659154 | 6501690015 | L&M | Closed | Reset York Central Recovery tank scale to zero. | 2017-02-10 |  |  |  |  | 2017-02-12 11:58 |  | Labor & Material | Closed | Y | Raul | Reed
2017-02-09 11:17 | 1-46632636600 | 6501690015 | L&M | Closed | CHILLER #7 OIL LEVEL ADJUSTMENT: Drain and Measure Oil in Shaft Seal Oil Drainage Tank Calculated Shaft Seal Leakage for Last Year Add New YORK "K" Oil (Furnished by DuPont) to Compressor Sump to bring running level up into Top Sight Glass. *The Oil Level is currently running in the Lower Sight Glass. Chiller could shutdown on Low Oil Pressure* | 2017-02-15 |  |  |  |  | 2017-02-11 11:17 |  | Custom Quote | Closed | Y | Raul | Reed
2017-02-09 11:07 | 1-46632636274 | 6501700761 | L&M | Closed | 6501700761 Chiller #9 Annual Maintenance 2017 Remove Refrigerant Sample for Chemical Analysis Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Furnish & Install Sight-Glass in Oil Return Line Change Compressor Oil w/ YORK J (Provided by DuPont) Disassemble Compressor Coupling and Check Cold Alignment Check Low-Speed Compressor Axial Thrust Reading Reassemble Coupling and Re-Check Compressor Coupling Cold Alignment Vacuum out Compressor Motor and Change Air Filters Change Oil in Compressor Motor Bearings (Provided by DuPont) Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Documents all tasks and Provide Comprehensive Report to DuPont | 2017-02-28 |  |  |  |  | 2017-02-11 11:07 |  | Custom Quote | Closed | Y | Raul | Reed
2017-02-03 12:52 | 1-46491125544 | 6501697258 | L&M | Closed | (PO 6501697258) CHILLER #8 EVAPORATOR WATERBOX REPAIRS: CLEAN AND PREPARE TUBE SHEET FOR STEEL EPOXY COATING APPLY BELZONA 1121 "SUPER XL-METAL" (PURCHASED UNDER DUPONT PO#: 6501690015) TO FILL IN PITS AND GOUGING CLEAN UP AND ENSURE EPOXY INTEGRITY AFTER 24HR CURE TIME | 2017-02-09 |  |  |  |  | 2017-02-05 12:52 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-02-01 15:21 | 1-46438155392 | 6501695980 | L&M | Closed | CHILLER #10 EDDYCURRENT EDDYCURRENT TESTING & ANALYSIS OF ALL EVAPORATOR & CONDENSER TUBES (1,582 TOTAL) FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED UPON COMPLETION *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED AND BRUSHED BEFORE TECHNICIAN ARRIVES UNIT MUST BE READY FOR TESTING WITH NO WAITING TIME* **THIS WORK IS CURRENTLY SCHEDULED FOR MARCH 9TH & 10TH ACCESS TO SITE AND POWERHOUSE WILL NEED TO BE ARRANGED & PROVIDED FOR THE TECHNICIAN BY DUPONT** | 2017-03-10 |  |  |  |  | 2017-02-03 15:21 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-02-01 15:01 | 1-46437169897 | 6501695977 | L&M | Closed | CHILLER #9 EDDY-CURRENT EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR & CONDENSER TUBES (1,582 TOTAL) FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED UPON COMPLETION. *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED AND BRUSHED BEFORE TECHNICIAN ARRIVES. UNIT MUST BE READY FOR TESTING WITH NO WAITING TIME.* **THIS WORK IS CURRENTLY SCHEDULED FOR FEB. 23RD & 24TH. ACCESS TO SITE AND POWERHOUSE WILL NEED TO BE ARRANGED & PROVIDED FOR THE TECHNICIAN BY DUPONT** | 2017-02-24 |  | 1-H7K9F6K | OTT4G2-ZBES | GACM127698 | 2017-02-03 15:01 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-01-30 14:38 | 1-46017866961 | 65001690015 | L&M | Closed | (Emergency PO) Chiller #8, erosion repair (pitting) to tube sheet in evaporator. | 2017-01-31 |  |  |  |  | 2017-02-01 14:41 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-01-27 11:44 | 1-45941594047 | 6501694234 | L&M | Closed | CHILLER #8 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#8 seal oil leak has been calculated at 4.92ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, O-RINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING **REFRIGERANT RECOVERY, EVACUATION, & RE-CHARGE IS COVERED UNDER OTHER QUOTES** | 2017-02-02 |  |  |  |  | 2017-01-29 11:44 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-01-27 11:29 | 1-45941194215 |  | L&M | Cancelled | CHILLER #8 SHAFT SEAL REPLACEMENT: Based on measurements take over the past 2 months CHILLER#8 seal oil leak has been calculated at 4.92ml/hr. This is double the factory recommended max leak rate of 2.23ml/hr (signal point for replacement). SCOPE: REMOVE COMPRESSOR COUPLING HUB REMOVE OLD SHAFT SEAL CLEAN & INSPECT INTERNAL COMPRESSOR SHAFT SURFACES CLEAN & RESUSE SHAFT SEAL COVER PLATE (if not damaged) INSTALL NEW SHAFT SEAL COMPONENTS (COLLAR, SEAL, SPRINGS, O-RINGS) CHECK FOR LEAKS & REASSEMBLE COUPLING **REFRIGERANT RECOVERY, EVACUATION, & RE-CHARGE IS COVERED UNDER OTHER QUOTES** | [5 empty] | 2017-01-29 11:29 |  | Custom Quote | Created In Error | Y | Raul | Dolphin
2017-01-26 08:13 | 1-45899325697 | 6501692933 | L&M | Closed | Chiller #8 Annual Maintenance 2017 Remove Refrigerant Sample for Chemical Analysis Refrigerant leak test chiller and document leaks found (repair minor leaks, if possible) Furnish and Change Compressor Oil Filter, and Oil Return Filter-Drier Change Compressor Oil w/ YORK J (Provided by DuPont) Disassemble Compressor Coupling and Check Cold Alignment Check Low-Speed Compressor Axial Thrust Reading Reassemble Coupling and Re-Check Compressor Coupling Cold Alignment Vacuum out Compressor Motor and Change Air Filters Change Oil in Compressor Motor Bearings (Provided by DuPont) Check all Chiller Controls, Safeties, and Low Voltage Electrical Connections Documents all tasks and Provide Comprehensive Report to DuPont *All other task, such as Recovery, Evacuation, Oil Sample, and Re-Charge are being performed under other Quotes* | 2017-02-06 |  |  |  |  | 2017-01-28 08:13 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-01-24 13:14 | 1-45848473572 | 6501691913 | L&M | Closed | YORK Centrifugal Chiller Annual Oil Analysis CHILLERS #7,#8,#9,#10: Remove Oil Samples from all YORK Centrifugals Send to Lab for Analysis Provide Analytical Reports w/ Recommendations for upcoming Annual Chiller Maintenance | 2017-01-25 |  |  |  |  | 2017-01-26 13:14 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-01-20 13:05 | 1-45765849262 | 6501691743 | L&M | Closed | CHILLER. #8 RELIEF TREE INSTALL Transfer Refrigerant to DuPonts Central Storage Tank according to EPA Specs. Record quantity recovered. Break Vacuum w/Nitrogen & Remove Current Relief Device. Install New 3-Way Valve, Relief Tree, and Relief Devices. Pressurize w/Nitrogen, Leak Test Entire Chiller. Evacuate Chiller & Perform Vacuum Hold Test. Recharge, Run, and Inspect Chiller Performance. ***DuPont will be responsible for providing all material to be installed and for constructing a scaffold that will allow the work to be carried out safely*** | 2017-02-16 |  |  |  |  | 2017-01-22 13:05 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-01-20 13:03 | 1-45765848899 | 6501691197 | L&M | Closed | CHILLER #8 EDDY-CURRENT EDDY-CURRENT TESTING & ANALYSIS OF ALL EVAPORATOR & CONDENSER TUBES (1,582 TOTAL). FINAL REPORT OF TUBE CONDITION WILL BE PROVIDED UPON COMPLETION. *NOTE: HEADS MUST BE DOWN AND TUBES CLEANED AND BRUSHED BEFORE TECHNICIAN ARRIVES. UNIT MUST BE READY FOR TESTING WITH NO WAITING TIME.* **THIS WORK IS CURRENTLY SCHEDULED FOR JAN. 27TH & 28TH. ACCESS TO SITE AND POWERHOUSE WILL NEED TO BE ARRANGED & PROVIDED FOR THE TECHNICIAN BY DUPONT ON SATURDAY THE 28TH.** | 2017-01-27 |  |  |  |  | 2017-01-22 13:03 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-01-19 13:37 | 1-45734478692 | 6501690015 | L&M | Closed | Consultive service of 1/18. Emergency work of 1/19. | 2017-01-19 |  |  |  |  | 2017-01-21 13:38 |  | Labor & Material | Closed | Y | Raul | Dolphin
2017-01-17 14:26 | 1-45677647587 | 6501690015 | L&M | Closed | CHILLER #8 LOW OIL LEVEL Add appropriate amount of YORK "J" Oil (Customer Supplied) to Chiller #8 to bring back to Normal Operating Level. Measure Seal Oil Leakage and Calculate Leak rates on #8,9,&10 to determine Condition of Shaft Seals. Make necessary Adjustments on Chiller #8's Vane Arm Assembly. Change and Tighten Fasteners. Apply Sealant to Actuator Motor Shaft. | 2016-12-28 |  | 1-FY0MJZY | OTT4G2-ZBES | GACM117864 | 2017-01-19 14:26 |  | Custom Quote | Closed | Y | Raul | Dolphin
2017-01-09 16:21 | 1-45487366293 | 6501690015 | L&M | Closed | Scheduling/consultive: Ruptured Disc replacements on qty 4 absorber chillers | 2017-01-10 |  |  |  |  | 2017-01-11 16:22 |  | Labor & Material | Closed | Y | Raul | Dolphin
2016-12-28 15:01 | 1-43713008400 |  | L&M | Cancelled | RUPTURED DISC REPAIR MOVING TO QUOTE 1K2OOT6G WHEN RAUL GETS PO Temporary holding spot for Mr Kevin Fraze | [5 empty] | 2016-12-30 15:02 |  | Customer Satisfaction | Customer Cancelled | N | Raul | Dolphin
2016-11-16 11:36 | 1-42462980933 | 6501663924 | L&M | Closed | CHILLERS #8, #9, #10 SOFTWARE UPGRADE: Coordinate with DuPont Operators to Shutdown and Lockout one Chiller at a time UPGRADE all three CHILLER MICROBOARDs to the LATEST Revision of CONTROL LOGIC SOFTWARE (v. C.03F.03) Unlock, Start Up, and Verify CHILLER Control Operation, and Ensure proper Communication with MICROGATEWAY Modbus Interface Chillers #8 and #9 are currently running with the Original Software C.03F.00 Chiller #10 is currently running Software Version C.03F.01 | 2016-11-29 |  |  |  |  | 2016-11-18 11:36 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-10-26 15:42 | 1-41561145038 | 6501611952 | L&M | Closed | ABSORBERS #2 & #3 PROVIDE MATERIAL: LITHIUM MOLYBDATE INHIBITOR based on recent SOLUTION Analysis to bring Levels back to Optimal. *Inhibitor levels in ABSORBERS #1 & #4 are within the Normal range and do not need adjustment at this time.* | [5 empty] | 2016-10-28 15:42 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-10-25 13:50 | 1-41528738833 |  | L&M | Cancelled | Material associated with PM - customer to supply. | [5 empty] | 2016-10-27 13:51 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2016-10-01 06:00 | 1-40855334427 |  | PSA | Closed | Preventive Maintenance | 2016-11-01 |  |  |  |  | 2016-10-01 07:40 | 1-HAKE4G3 | Scheduled Service | Closed | N | Raul | Administrator
2016-09-16 14:23 | 1-38992535910 | 6501638582 | L&M | Closed | Chiller #9 Fault; transducer issue | 2016-09-19 |  |  |  |  | 2016-09-18 14:24 |  | Labor & Material | Closed | Y | Raul | Dolphin
2016-08-25 11:03 | 1-37498214070 | 6501630558 | L&M | Closed | ABSORBER #1 "AUTO-PURGE FAILURE" Troubleshooting, Leak Test & Repairs: Completely DISASSEMBLE Purge Header REMOVE and REPLACE Faulty Solenoid Valve (1SOL) CLEAN all PIPING and THREADS DISASSEMBLE Automatic Ball Valve (2SOL) CLEAN and Re-Assemble RE-ASSEMBLE all PIPING w/ New Sealant and Flange Gasket. REPLACE PURGE CHECK VALVE and TRANSDUCER PRESSURIZE Purge Header and Verify that it is Leak Free and Dry Return Auto-Purge Operation to "AUTOMATIC" | 2016-08-25 |  | GLCM157836 | YPC ST 22G | GLCM157836 | 2016-08-27 11:03 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-08-22 14:07 | 1-37410017994 |  | L&M | Cancelled | Absorber #1; Auto Purge Failure. Trouble shooting, leak test and repair. | [5 empty] | 2016-08-24 14:09 |  | Labor & Material | Customer Cancelled | Y | Raul | Dolphin
2016-08-03 12:07 | 1-36853244088 | 6501620987 | L&M | Closed | ABSORBER #3 Due to the HIGH FREQUENCY of PURGES while Operational, along with CHEMICAL ANALYSIS, Recommend INSTALLING LITHIUM NITRATE TYPE INHIBITOR Perform LEAK TEST of PURGE TREE HEADER and REPAIR any LEAKS FOUND ABSORBER #3 should REMAIN OPERATING in order to properly TREND PURGE FREQUENCY, and determine if there are other possible causes | 2016-08-11 |  |  |  |  | 2016-08-05 12:07 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-08-01 14:15 | 1-36780001028 | 6501620268 | L&M | Closed | Chris Cooper requested installation of relief device on central recovery liquid line. | 2016-08-02 |  |  |  |  | 2016-08-03 14:20 |  | Labor & Material | Closed | Y | Raul | Dolphin
2016-08-01 06:00 | 1-35841204337 |  | PSA | Closed | Preventive Maintenance | 2016-08-18 |  |  |  |  | 2016-07-03 14:04 | 1-BQV79A9 | Scheduled Service | Closed | N | Diane | Administrator
2016-07-26 07:45 | 1-36516053617 | 6501620268 | L&M | Closed | Due to weather event, Chillers #8 and 9 will not restart- power failure. Troubleshoot and repair. | 2016-07-27 |  |  |  |  | 2016-07-28 07:48 |  | Labor & Material | Closed | Y | Raul | Dolphin
2016-07-20 13:54 | 1-36363184896 | 6501616658 | L&M | Closed | ABSORBER #1 Due to High Concentration of Suspended Solids after Solution Pump Failure, FILTERING is REQUIRED RELOCATE Canister from ABS#2 to ABS#3 INSTALL NEW HOSES, FLANGE and BALL VALVE (on VP7) FURNISH 18 New PALL Bromide Solution FILTERS to REPLENISH Supply onsite. (6 Filters per Changeout) REMOVE and REPLACE current clogged Filters CLEAN out Canister EVACUATE and RETURN to Service REPLACE FILTERS as needed until SUSPENDED SOLIDS in SOLUTION is at ACCEPTABLE LEVELS | 2016-07-22 |  |  |  |  | 2016-07-22 13:54 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-07-08 14:33 | 1-36028109391 | Raul Cozza | L&M | Closed | ABSORBER #2 FURNISH 18 New PALL Bromide Solution FILTERS to REPLENISH Supply onsite (6 Filters per Changeout) REMOVE and REPLACE current clogged Filters CLEAN out Canister EVACUATE and RETURN to Service | 2016-07-21 |  |  |  |  | 2016-07-10 14:33 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-07-07 11:09 | 1-35974893871 | 6501611959 | L&M | Closed | ABSORBER #3 REMOVE and REPLACE Faulty Solenoid Valve (1SOL) CLEAN Purge Header Return Purge Operation back to AUTOMATIC OPERATORS will no longer need to worry about MANUALLY Purging PURGE TANK | 2016-07-07 |  |  |  |  | 2016-07-09 11:09 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-07-06 11:16 | 1-35942212834 | 6501611952 | L&M | Closed | ABSORBERS #2, #3, #4 LITHIUM MOLYBDATE INHIBITOR based on recent SOLUTION Analysis to bring Levels back to Optimal. | 2016-07-06 |  |  |  |  | 2016-07-08 11:16 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-07-05 11:20 | 1-35911259064 | 6501611969 | L&M | Closed | ABSORBER #1 Furnish NEW Motor Assembly for the Main Solution Pump (This is the entire Pump with exception on the Volute and Impeller) ** The cost of installing the Pump and all Labor associated with bringing ABSORBER #1 back online will be covered by the original JCI Quote # 1-G8EH8ER. ** ** For the price of both Quotes, DuPont will have 1 NEW Solution Pump w/Motor Installed & 1 Rebuilt Solution Pump w/Motor, left onsite as a Spare ** **** Lead Time for the NEW Motor Assembly from the Factory is currently 3 Weeks **** | 2016-07-08 |  | 2670590 |  |  | 2016-07-07 11:20 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-07-01 06:00 | 1-34566790831 |  | PSA | Closed | Preventive Maintenance | 2016-07-19 |  |  |  |  | 2016-06-03 10:00 | 1-BQV79A9 | Scheduled Service | Closed | N | Diane | Administrator
2016-06-23 12:44 | 1-35376456584 |  | L&M | Closed | Per Chris Cooper: Removal and re-installation of Central SUVA Storage Tank Liquid Line Relief valve 315XRV00219XXX for testing. | 2016-06-23 |  |  |  |  | 2016-06-25 12:48 |  | Labor & Material | Closed | Y | Diane | Dolphin
2016-06-23 12:42 | 1-35376456034 | 6501608975 | L&M | Closed | ABSORBER #1 Remove and Replace Main Solution Pump Wearing Rings Remove and Replace Seized Studs in Pump Casing Thoroughly Clean all Pump Parts Furnish and Install New Pump Motor Carbon Graphite Bearings Re-Assemble Pump with Original Impeller Re-Install Pump with New Casing Gasket Install new Motor Contactor and Overload Assembly and Re-wire the pump Remove and Replace Fouled Sight-glasses in Absorber Section Evacuate Absorber Re-Install removed Solution through Filters Reset Valves to Original Positions Startup and Purge Absorber Ensure proper Operation | 2016-07-28 |  | 2670590 |  |  | 2016-06-25 12:42 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-06-20 13:07 | 1-35270891278 | 6501605952 | L&M | Closed | ABSORBER #1 Machining will be performed on the Main Solution Pump Rotor Assembly to repair worn parts and return to design specs. Have Impeller Balance verified. (If unbalanced an additional quote will be provided). | 2016-06-27 |  |  |  |  | 2016-06-22 13:07 |  | Custom Quote | Closed | Y | Christopher | Dolphin
2016-06-09 07:10 | 1-34850489163 | 6501600380 PO attached | L&M | Closed | ABSORBER#1 MAIN SOLUTION PUMP INSPECTION Transfer Solution to Generators and Drums Disconnect and Pull Main Solution Pump Inspect, Clean out Solution, Disassemble Pump Inspect Bearings, Impeller, and Pump Seals Install Blank on Pump Volute until Additional Repairs are made | 2016-06-17 |  |  |  |  | 2016-06-11 07:10 |  | Custom Quote | Closed | Y | Raul | Dolphin
2016-06-05 19:07 | 1-34691988271 | 6501598682 | L&M | Closed | Inspect and Repair Chiller #8 Evaporator issues, ESL Powerhouse (E315) | 2016-06-23 |  | 1-FY0MJZY | OTT4G2-ZBES | GACM117864 | 2016-06-07 19:11 |  | Labor & Material | Closed | Y | Diane | Dolphin
2016-06-01 06:00 | 1-33644815808 |  | PSA | Closed | Preventive Maintenance Absorber #1 has been under repair. Unable to perform PM. | 2016-07-18 |  |  |  |  | 2016-05-03 09:34 | 1-BQV79A9 | Scheduled Service | Closed | N | Diane | Administrator
2016-05-27 13:16 | 1-34404994575 | Diane Skilton | L&M | Closed | Chiller #10, not loading. | 2016-05-27 |  | 1-FNV12L6 | OTT4G2-ZBES | GACM127699 | 2016-05-29 13:19 |  | Labor & Material | Closed | Y | Diane | Dolphin
2016-05-25 07:08 | 1-34287950346 |  | L&M | Closed | Abs #4; high solution concentration. KF | 2016-05-25 |  | 2670593 | YPC-ST-22G-46-C-X-A | GNCM94230017 | 2016-05-27 07:11 |  | Labor & Material | Closed | Y | Raul | Dolphin
2016-05-13 15:27 | 1-33993104959 | 6501590122 | L&M | Closed | repair limit switch on chiller#10 | 2016-05-13 |  |  |  |  | 2016-05-15 15:29 |  | Labor & Material | Closed | Y | Diane | Reed
2016-05-13 11:09 | 1-33983397168 |  | L&M | Closed | -replace relief devices on chiller#7 -additional Rupture Disk Replacement on Chiller #7 and its Central Storage tank. | 2016-05-16 |  |  |  |  | 2016-05-15 11:14 |  | Labor & Material | Closed | Y | Raul | Reed
2016-05-01 06:00 | 1-32243121739 |  | PSA | Closed | Preventive Maintenance | 2016-05-18 |  |  |  |  | 2016-04-03 10:58 | 1-BQV79A9 | Scheduled Service | Closed | N | Diane | Administrator
2016-04-21 14:14 | 1-33069099287 | 6501580874 | L&M | Closed | ROOFTOP CHILLER E336 SERVICE SCHEDULED FOR 4/30 RUSSELL YETTER CONTACT JIM TIDWELL-302.218.9528 | 2016-04-30 |  |  |  |  | 2016-04-23 14:17 |  | Labor & Material | Closed | Y | Diane | Reed
2016-04-05 08:37 | 1-32345011806 |  | L&M | Closed | Chiller #7 - Troubleshoot Oil Separator | 2016-04-05 |  |  |  |  | 2016-04-07 08:38 |  | Labor & Material | Closed | Y | Diane | Morris
2016-03-30 14:06 | 1-32160999861 |  | L&M | Cancelled | Chiller #7 Startup - Trailing cost against Maintenance SR | [5 empty] | 2016-04-01 14:17 |  | Customer Satisfaction | Created In Error | N | Raul | Morris
2016-03-07 14:17 | 1-31515692746 | 6501560949 | L&M | Closed | Chiller #7 - Leak Repair | 2016-03-10 |  |  |  |  | 2016-03-09 14:18 |  | Labor & Material | Closed | Y | Raul | Morris
2016-02-22 09:28 | 1-30777898703 | 6501537255 | L&M | Closed | Chiller 7 (ESL E315) - Labor continuation (Rupture disks) | 2016-02-24 |  |  |  |  | 2016-02-24 09:28 |  | Labor & Material | Closed | Y | Raul | Morris
2016-02-12 08:45 | 1-29274542300 | 6501549099 | L&M | Closed | Remove samples of compressor oil and refrigerant for chemical analysis. Refrigerant leak test chiller and document leaks found (repair “minor” leaks, if possible). Transfer R-134A to storage tank for accurate weight of charge (Leaving 5psi on Chiller). Furnish and change compressor oil filters, and all driers. Furnish and change gearbox oil filters and oil (*Gear/Motor Oil furnished by DuPont*). Inspect gears and internal gearbox components. Disassemble motor coupling and check cold alignment. Repack motor coupling with grease and reassemble. Disassemble Compressor coupling. Check compressor axial thrust readings. Check compressor coupling cold alignment. Reassemble coupling. Vacuum out compressor motor. Brush clean all oil cooler tubes (Gear & Compressor). Transfer R-134A charge back into Chiller. | 2016-03-31 |  |  |  |  | 2016-02-14 08:45 |  | Custom Quote | Closed | Y | Raul | Morris
2016-02-10 15:52 | 1-29228476787 | 6501537255 | L&M | Closed | Chiller 7 (ESL E315) - Labor continuation | 2016-02-12 |  |  |  |  | 2016-02-12 15:54 |  | Labor & Material | Closed | Y | Raul | Morris
2016-02-04 14:12 | 1-29066059613 | 6501545663 | L&M | Closed | Eddy-Current Testing performed on all Evaporator (1852) and Condenser (2590) Tubes. Detailed report of analysis will be provided to DuPont. Water Box Heads must be removed, all tubes thoroughly cleaned, and scaffolding set up, before technician arrives | 2016-03-01 |  |  |  |  | 2016-02-06 14:12 |  | Custom Quote | Closed | Y | Raul | Morris
2016-02-02 12:48 | 1-28998918974 | 6501541957 | L&M | Closed | Complete replacement of faulty and obsolete Compressor Pneumatic Vane Actuator w/ integral Pilot Positioner. (The new actuator is the latest model of its kind, thereby making replacements parts readily available in the future.) Replace control air pressure throttling valve. Replace any pneumatic tubing or fittings necessary. Replace pneumatic air filters on for control air and main piston air. Set pressure regulators to design pressures. Set up correct position stroke length and span. Calibrate controls for proper Vane positioning and stable control of Compressor. Check control and operation of both Interstage and Hot Gas Bypass Bypass valves. Ensure that the are working as per design and in conjunction with Vane Actuator. | 2016-03-18 |  |  |  |  | 2016-02-04 12:48 |  | Custom Quote | Closed | Y | Raul | Morris
2016-01-29 10:31 | 1-28882156385 | 6501537255 | L&M | Closed | Chiller 7 (ESL E315) - Labor continuation | 2016-02-01 |  |  |  |  | 2016-01-31 10:33 |  | Labor & Material | Closed | Y | Raul | Morris
2016-01-21 13:41 | 1-28657093467 | 6501537307 | L&M | Closed | Furnish qty-4 rolls of gasket material p/n 028-03242-050. Shipping included. | [5 empty] | 2016-01-23 13:41 |  | Custom Quote | Closed | Y | Christopher | Morris
2016-01-18 20:57 | 1-28577700955 | 6501537148 | L&M | Closed | CHILLER #7 Capacity Control Inspection, Diagnosis, and Evaluation of any Repairs Necessary. - This work is in response to DuPont Powerhouse Operators reporting erratic operation of Chiller #7's Capacity Control Pre-Rotation Vanes and a Vibration Shutdown Fault. - If substantial repairs are determined to be necessary, a separate quote will be provided to cover the additional Labor and Materials involved. | 2016-01-20 |  |  |  |  | 2016-01-20 20:57 |  | Custom Quote | Closed | Y | Raul | Morris
2016-01-18 13:04 | 1-28571115916 | 6501537255 | L&M | Closed | Due:1/18 Desc:Chiller #7, evaluate replacement of rupture discs. Svc Hrs:N/A Access:N/A Contact:Raul Cozza 302-695-7842 Caller:JCI mech Kevin Fraze 302-353-0315 | 2016-01-29 | [6 empty] | Labor & Material | Closed | Y | Raul | Shah
2016-01-12 15:12 | 1-28429060770 |  | L&M | Cancelled | Chiller #7 - Look over vanes control | [5 empty] | 2016-01-14 15:13 |  | Labor & Material | Created In Error | Y | Raul | Morris
2015-11-05 08:43 | 1-26693184827 | 6501505894 | L&M | Closed | Molybdate Corrosion Inhibitor in quantities specified by recent Lithium Bromide lab analysis for each ABSORBER. *This quote is for MATERIAL ONLY. Labor for adding Inhibitor will be covered under the current Maintenance Contract.* | [5 empty] | 2015-11-07 08:43 |  | Custom Quote | Closed | Y | Raul | Morris
2015-10-30 13:08 | 1-26526940839 |  | L&M | Closed | Replace defective Purge Solenoid Valves (1SOL) on ABSORBER #1 and ABSORBER #2. Current valves were not properly sealing when closed, causing the Absorber Logic Board to cease "Smart" Auto-Purge Operation, and requiring Operators to Manually purge the Purge Tank while in Absorbers are in operation. Return Purges to Auto-Mode and Inspect Operation. **Quote DOES NOT include the price of the New Solenoid Valves. These were already purchased and billed to DuPont on a previous job.** | 2015-10-30 |  |  |  |  | 2015-11-01 13:08 |  | Custom Quote | Closed | Y | Raul | Morris
2015-10-03 06:05 | 1-25700650894 |  | PSA | Closed | Preventive Maintenance | 2015-11-16 |  |  |  |  | 2015-10-05 06:05 | 1-BQV79A9 | Scheduled Service | Closed | N | Diane | Administrator
2015-09-24 07:50 | 1-25343174313 | 6501485253 | L&M | Closed | Furnish qty-12 York Oil Filters p/n 025-11225-000 Shipping included | [5 empty] | 2015-09-26 07:51 |  | Custom Quote | Closed | Y | Christopher | Morris
2015-09-14 10:58 | 1-25030777306 |  | L&M | Closed | ABS#1 - Troubleshoot Smart Purge Repair | 2015-09-18 |  |  |  |  | 2015-09-16 10:59 |  | Labor & Material | Closed | Y | Raul | Morris
2015-09-14 10:54 | 1-25030508963 | Raul Cozza | L&M | Closed | ABS#4 - Troubleshoot main solution pump. | 2015-09-15 |  |  |  |  | 2015-09-16 10:56 |  | Labor & Material | Closed | Y | Raul | Morris
2015-09-08 13:34 | 1-24856075192 |  | L&M | Closed | Absorber #2 in alarm | 2015-09-15 |  |  |  |  | 2015-09-10 13:37 |  | Labor & Material | Closed | Y | Raul | Morris
2015-08-19 12:18 | 1-24241567558 | 6501469316 | L&M | Closed | Troubleshoot issue with ABS#4 – Motor tripping off on overloads - ABS#4 Refrig Pump Motor Removal, Rebuild and Replacement with new motor. | 2015-08-27 |  |  |  |  | 2015-08-21 12:23 |  | Labor & Material | Closed | Y | Raul | Morris
2015-08-17 16:12 | 1-24187391580 | 6501469316 | L&M | Closed | YORK Parts ONLY for ABSORBER #4 (All Parts are New and should be Replaced when Motor/Rotor/Impeller Assembly is pulled): Refrigerant Pump Motor Motor Front and Rear Bearings Pump Casing Wearing Ring Motor Side Wearing Ring Impeller Fastening Hardware Pump Casing Gasket Motor Contactor & Overload Assembly All parts are available at are Baltimore Parts Center in Limited Quantities. | [5 empty] | 2015-08-19 16:12 |  | Custom Quote | Closed | Y | Raul | Morris
2015-08-17 10:46 | 1-24173921374 | 6501524856 | L&M | Closed | Chiller 8 - Troubleshoot PVR issue | 2015-08-19 |  |  |  |  | 2015-08-19 10:49 |  | Labor & Material | Closed | Y | Raul | Morris
2015-08-05 14:47 | 1-23822214702 | 6501469316 | L&M | Closed | Troubleshoot Absorber Ref. Pump #4. | 2015-08-10 |  | 2670593 | YPC-ST-22G-46-C-X-A | GNCM94230017 | 2015-08-07 14:52 |  | Labor & Material | Closed | Y | Raul | Morris
2015-06-11 09:53 | 1-22014279916 | 6501441353 | L&M | Closed | Defective auto purge actuator. | 2015-06-12 |  |  |  |  | 2015-06-13 09:54 |  | Labor & Material | Closed | Y | Raul | Morris
2015-06-05 10:24 | 1-21813419439 |  | L&M | Closed | Building 336 - Troubleshoot chiller operation | 2015-06-20 |  |  |  |  | 2015-06-07 10:26 |  | Labor & Material | Closed | Y | Raul | Morris
2015-06-02 10:33 | 1-21689841312 | 6501455439 | L&M | Closed | Chiller #9 - Oil leak | 2015-06-02 |  |  |  |  | 2015-06-04 10:34 |  | Labor & Material | Closed | Y | Raul | Morris
2015-05-07 09:37 | 1-20800016829 | 6501434411 | L&M | Closed | Panel for Aborsober #1 blew out. | 2015-05-18 |  |  |  |  | 2015-05-09 09:38 |  | Labor & Material | Closed | Y | Raul | Morris
2015-05-07 09:00 | 1-20798887284 | 6501426534 | L&M | Closed | Furnish qty-1 55 gallon drum of new York "K" oil. Shipping included. | [5 empty] | 2015-05-09 09:00 |  | Custom Quote | Closed | Y | Raul | Morris
2015-05-06 13:35 | 1-20772877187 | 6501426354 | L&M | Closed | Supply 36 Solution filters for Absorber #2. | [5 empty] | 2015-05-08 13:35 |  | Custom Quote | Closed | Y | Raul | Morris
2015-05-01 06:00 | 1-19763475372 |  | PSA | Closed | Preventive Maintenance | 2015-05-08 |  |  |  |  | 2015-04-03 09:14 | 1-4T3MX42 | Scheduled Service | Closed | N | Diane | Administrator
2015-04-14 13:15 | 1-20136654284 | LOX612634 | L&M | Closed | Chiller #7 low oil pressure | 2015-04-14 |  |  |  |  | 2015-04-16 13:16 |  | Labor & Material | Closed | Y | Raul | Morris
2015-04-01 06:00 | 1-18893440282 |  | PSA | Closed | Preventive Maintenance | [5 empty] | 2015-03-03 08:14 | 1-4T3MX42 | Scheduled Service | Closed | N | Diane | Administrator
2015-02-06 09:39 | 1-18202458640 | LOX611091 | L&M | Closed | Furnish and install qty-1 new compressor shaft seal on Chiller #7. m/n OM3000 s/n MRP626904 Lock out / Tag out all energy sources Recover refrigerant into chiller reciever Disconnect coupling between gearbox and compressor Check and record compressor alignment readings Check and record compressor axial thrust reading Install new compressor shaft seal Reassemble compressor coupling Pressure test and evacuate chiller Recharge chiller with recovered refrigerant Exclusions: Additional refrigerant charge if needed Leak repairs other than compressor shaft seal | 2015-02-25 |  |  |  |  | 2015-02-08 09:39 |  | Custom Quote | Closed | Y | Raul | Morris
2015-02-01 06:00 | 1-17237691041 |  | PSA | Closed | Preventive Maintenance | 2015-03-20 |  |  |  |  | 2015-01-03 10:54 | 1-4T3MX42 | Scheduled Service | Closed | N | Diane | Administrator
2015-01-23 15:32 | 1-17767611385 | LOX610743 | L&M | Closed | Material Only - Provide (6) 392 10719 000 KIT, FILTER and (6) 028 08312 001 KIT, REPL GASKETS | [5 empty] | 2015-01-25 15:32 |  | Custom Quote | Closed | Y | Raul | Morris
2015-01-16 08:49 | 1-17578850663 | LOX610534 | L&M | Closed | Furnish and install qty-4 new transducers and qty-8 new temperature sensors on Chiller #9. Connect all wiring and verify operation of each device. | 2015-01-22 |  |  |  |  | 2015-01-18 08:49 |  | Custom Quote | Closed | Y | Raul | Morris
2014-12-10 13:06 | 1-16741327980 | LOX609895 | L&M | Closed | Furnish gasket material for York Absorption chillers. qty-300 ft of Bulb gasket material qty-25 ft of baffle gasket material | [5 empty] | 2014-12-12 13:06 |  | Custom Quote | Closed | Y | Christopher | Morris
2014-12-01 06:00 | 1-15599227365 |  | PSA | Closed | Preventive Maintenance | 2015-06-22 |  |  |  |  | 2014-11-03 11:59 | 1-4T3MX42 | Scheduled Service | Closed | N | Diane | Administrator
2014-10-31 14:22 | 1-15566817791 |  | L&M | Closed | Rebuild compressor on Chiller #9. m/n OTT4G2-ZBES s/n GACM117864 Lock out / tag out all energy sources Recover and store all refrigerant using plant recovery system Disconnect compressor coupling Disconnect all compressor piping Set up rigging and lower compressor to ground Record compressor thrust and runout readings Disassemble entire compressor and evaluate all parts Furnish and install new compressor bearings and gaskets Record compressor thrust and runout readings after rebuild Rig compressor onto chiller Reconnect all piping Pressure test system with nitrogen and leak test Check and adjust motor alignment as needed Reassemble compressor coupling Evacuate system and charge with recovered refrigerant Run chiller and check operation Provide all documentation Note: Pricing per chiller. | 2015-01-30 |  |  |  |  | 2014-11-02 14:42 |  | Shared Resource to Projects | Closed | N | Raul | Morris
2014-10-15 14:41 | 1-15113570309 | LOX608154 | L&M | Cancelled | Rebuild compressor on Chiller #9. m/n OTT4G2-ZBES s/n GACM117864 Lock out / tag out all energy sources Recover and store all refrigerant using plant recovery system Disconnect compressor coupling Disconnect all compressor piping Set up rigging and lower compressor to ground Record compressor thrust and runout readings Disassemble entire compressor and evaluate all parts Furnish and install new compressor bearings and gaskets Record compressor thrust and runout readings after rebuild Rig compressor onto chiller Reconnect all piping Pressure test system with nitrogen and leak test Check and adjust motor alignment as needed Reassemble compressor coupling Evacuate system and charge with recovered refrigerant Run chiller and check operation Provide all documentation Note: Pricing per chiller. | [5 empty] | 2014-10-17 14:41 |  | Custom Quote | Created In Error | Y | Raul | Morris
2014-10-15 14:20 | 1-15112969639 | LOX608468 | L&M | Closed | Parts only. Provide Two Three way Valves for the installation of dual relief valves on Chiller #8 and #9 | [5 empty] | 2014-10-17 14:20 |  | Custom Quote | Closed | Y | Raul | Morris
2014-10-15 14:14 | 1-15112209612 | LOX608467 | L&M | Closed | Provide Corrosion Inhibitor for the Absorption Chillers Per the Solution Analysis. Provide the labor to charge the inhibitor into the Absorbers. | 2014-10-31 |  |  |  |  | 2014-10-17 14:14 |  | Custom Quote | Closed | Y | Raul | Morris
2014-10-08 06:05 | 1-14907457363 |  | PSA | Closed | Preventive Maintenance | 2014-11-04 |  |  |  |  | 2014-10-10 06:05 | 1-4T3MX42 | Scheduled Service | Closed | N | CAROL | Administrator
2014-10-07 13:33 | 1-14883658051 |  | L&M | Cancelled | Pressurize the absorbers | [5 empty] | 2014-10-09 13:34 |  | Labor & Material | Created In Error | Y | Raul | Morris
2014-08-08 17:52 | 1-13001254857 | LOX606511 | L&M | Closed | De-crystalize ABS #2 in the powerhouse (PO Req##68377) | 2014-08-19 |  |  |  |  | 2014-08-10 17:52 |  | Labor & Material | Closed | Y | Christopher | Morris
2014-08-01 06:00 | 1-11933135666 |  | PSA | Closed | Preventive Maintenance | 2014-08-20 |  |  |  |  | 2014-07-03 09:09 | 1-4T3MX42 | Scheduled Service | Closed | N | CAROL | Administrator
2014-07-02 16:08 | 1-11975635560 | LGGC22452 | L&M | Closed | Troubleshoot the E336 Chiller | 2014-07-02 |  |  |  |  | 2014-07-04 16:12 |  | Labor & Material | Closed | Y | Mark | Morris
2014-06-30 15:35 | 1-11907374430 | LOX606606 | L&M | Closed | Chiller #7 oil leak | 2014-07-02 |  |  |  |  | 2014-07-02 15:36 |  | Labor & Material | Closed | Y | Raul | Morris
2014-06-27 08:16 | 1-11825182709 | LOX606593 | L&M | Closed | Absorber #4 - Solution pump tripped on overload. | 2014-06-27 |  |  |  |  | 2014-06-29 08:16 |  | Labor & Material | Closed | Y | Raul | Morris
2014-06-25 15:01 | 1-11773195658 | LOX605366 | L&M | Closed | Absorber #2 crystallized. Steam shut off valvle is passing | 2014-06-25 |  |  |  |  | 2014-06-27 15:03 |  | Labor & Material | Closed | Y | Raul | Morris
2014-05-01 06:00 | 1-9803714643 |  | PSA | Closed | Preventive Maintenance | 2014-06-24 |  |  |  |  | 2014-04-03 08:28 | 1-359HQG7 | Scheduled Service | Closed | N | CAROL | Administrator
2014-03-26 11:19 | 1-9687624328 | LOX597574 | L&M | Closed | INCLUDED • Disassemble and remove existing Pin Relief Valve. • Provide and install a 3 Way Isolation valve • Provide and install two rupture disk and Disk Holders. • Provide new Gaskets and Bolts Reinstall Spring loaded relief disks after the rupture disks. NOT INCLUDED • Piping modifications needed to connect out of the dual relief assembly to the common header • New spring relief Valve Partial Billing of $13016.54 PO from Dupont Remaining amount of $4000.00 will be billed when valves come in | 2014-03-22 |  |  |  |  | 2014-03-28 11:19 |  | Custom Quote | Closed | Y | Diane | Walsh
2014-03-13 13:04 | 1-9416568627 | LGGC21128 | L&M | Closed | Replace all Transducers and Temperature Sensors on CH 10 Order a backup set of sensors and transducers for spare parts. | 2014-03-22 |  |  |  |  | 2014-03-15 13:04 |  | Custom Quote | Closed | Y | Raul | Walsh
2014-03-06 09:48 | 1-9307117648 | LOX600371 | L&M | Closed | Furnish qty-1 55 gallon drum of new York "J" oil. Furnish qty-3 5 gallon containers of new York "J" oil. Shipping included. Pricing: York "J" oil 5 gallon container $756.00 each. York "J" oil 55 gallon container $8,427.00 | [5 empty] | 2014-03-08 09:48 |  | Custom Quote | Closed | Y | Diane | Walsh
2014-02-14 11:34 | 1-8972377924 | LGGC20932 | L&M | Closed | Tube Plugging during Eddy Current Test on the Evaporator Tubes CH#6 | 2014-02-14 |  |  |  |  | 2014-02-16 11:34 |  | Custom Quote | Closed | Y | Raul | Johnson
2014-02-12 11:17 | 1-8936306112 | LOX598048 | L&M | Closed | Eddy Current test the condenser and sub cooler tubes on Chiller #6 Provide a detailed report on the condition of the tubes The tubes must be cleaned prior to testing. Exclusions Tube cleaning Tube Plugging | [5 empty] | 2014-02-14 11:17 |  | Custom Quote | Closed | Y | Raul | Johnson
2014-02-04 14:12 | 1-8817876517 | LOX598757 | L&M | Closed | Perform Eddy Current Test on the Evaporator Tubes CH#6 Provide a detailed report of the test Tubes must be cleaned prior to testing Exclusions Tube Cleaning Tube Plugging Head Removal | 2014-02-14 |  |  |  |  | 2014-02-06 14:12 |  | Custom Quote | Closed | Y | Raul | Johnson
2014-02-01 06:00 | 1-8239142748 |  | PSA | Closed | Preventive Maintenance | 2014-04-23 |  |  |  |  | 2014-01-03 08:31 | 1-359HQG7 | Scheduled Service | Closed | N | CAROL | Administrator
2014-01-21 08:42 | 1-8552733559 | LOX597975 | L&M | Closed | * Mobilize/lock out equipment *Recover Refrigerant *Dissassemble and Inspect Compressor. Record Existing Tolerances *Reassemble Compressor with new bearings, seals, and gaskets *Realign motor to compressor *Pressure test and leak test the unit *Evacuate and recycle the refrigerant into the unit *Start, Teat and Adjust Not Included *Additional Refrigerant *Required Scaffolding | 2014-03-25 |  |  |  |  | 2014-01-23 08:42 |  | Custom Quote | Closed | Y | Raul | Johnson
2014-01-20 10:08 | 1-8542784246 | LGGC20800 | L&M | Closed | Plugging a tube on a chiller | 2014-01-21 |  |  |  |  | 2014-01-22 10:09 |  | Labor & Material | Closed | Y | Raul | Williams
2014-01-10 09:11 | 1-8412597585 | Raul Cozza | L&M | Closed | *Eddy current test the condenser tubes * Provide report on the condition of the tubes * Tubes must be cleaned prior to the test Exclusions Tube cleaning Head removal Tube plugging | 2014-01-13 |  |  |  |  | 2014-01-12 09:11 |  | Custom Quote | Closed | Y | Raul | Johnson
2014-01-08 11:53 | 1-8369169561 |  | L&M | Cancelled | Perform Eddy Current Test on condenser tubes for Chiller #7 | [5 empty] | 2014-01-10 11:53 |  | Custom Quote | Created In Error | Y | Raul | Johnson
2014-01-08 07:29 | 1-8363544161 | LOX597574 | L&M | Closed | INCLUDED • Disassemble and remove existing Pin Relief Valve. • Provide and install a 3 Way Isolation valve • Provide and install two rupture disk and Disk Holders. • Provide new Gaskets and Bolts Reinstall Spring loaded relief disks after the rupture disks. NOT INCLUDED • Piping modifications needed to connect out of the dual relief assembly to the common header • New spring relief Valve | [5 empty] | 2014-01-10 07:29 |  | Custom Quote | Closed | Y | TOM | Johnson
2013-12-01 06:00 | 1-7368924475 |  | PSA | Closed | Preventive Maintenance | 2014-01-21 |  |  |  |  | 2013-11-03 08:00 | 1-359HQG7 | Scheduled Service | Closed | N | CAROL | Administrator
2013-10-04 13:23 | 1-7276250083 |  | L&M | Closed | Temp adjustment Bldg E336 | 2013-10-05 |  |  |  |  | 2013-10-06 13:34 |  | Labor & Material | Closed | Y | CAROL | Johnson
2013-10-02 12:58 | 1-7265537958 | LOX589867 | L&M | Closed | Furnish Lithium Molybdate inhibitor in qty-3 absorption chillers as needed based on analysis results. | [5 empty] | 2013-10-04 12:58 |  | Custom Quote | Closed | Y | TOM | Johnson
2013-08-20 18:54 | 1-7103037037 | LMCH11867 | L&M | Closed | Absorber #4 micro gateway is not communicating | 2013-08-28 |  |  |  |  | 2013-08-22 18:56 |  | Labor & Material | Closed | Y | TOM | Johnson
2013-08-01 06:00 | 1-6925972819 |  | PSA | Closed | Preventive Maintenance | 2013-09-06 |  |  |  |  | 2013-07-03 12:26 | 1-359HQG7 | Scheduled Service | Closed | N | TOM | Administrator
2013-07-16 08:56 | 1-6969912043 | LOX589867 | L&M | Closed | ABSORBER CHILLER #2 DOWN | 2013-07-16 |  |  |  |  | 2013-07-18 08:58 |  | Labor & Material | Closed | Y | TOM | Johnson
2013-07-10 08:42 | 1-6950972053 | LOX591186 | L&M | Closed | Add lithium Bromide to absorber #2 | 2013-07-31 |  |  |  |  | 2013-07-12 08:42 |  | Custom Quote | Closed | Y | Tom | Johnson
2013-06-26 11:26 | 1-6900000669 | LOX589867 | L&M | Closed | Labor to install inhibitor in Absorber Chiller | 2013-06-26 |  |  |  |  | 2013-06-28 11:27 |  | Labor & Material | Closed | Y | TOM | Johnson
2013-06-25 11:41 | 1-6895023658 | LOX589867 | L&M | Closed | PROBLEM WITH ABSORBER CHILLER #9 | 2013-06-25 |  |  |  |  | 2013-06-27 11:43 |  | Labor & Material | Closed | Y | TOM | Johnson
2013-06-18 10:53 | 1-6869910154 | LOX590515 | L&M | Closed | Furnish Lithium Molybdate inhibitor in qty-3 absorption chillers as needed based on analysis results. | [5 empty] | 2013-06-20 10:53 |  | Custom Quote | Closed | Y | TOM | Johnson
2013-06-05 07:22 | 1-6829119961 | LOX589867 | L&M | Closed | DE-CRYSTALIZED ABSORBER #2 | 2013-06-05 |  |  |  |  | 2013-06-07 07:25 |  | Labor & Material | Closed | Y | Tom | Johnson
2013-05-01 06:00 | 1-6608989438 |  | PSA | Closed | Preventive Maintenance | 2013-05-03 |  |  |  |  | 2013-04-03 08:36 | 1-2GEM8RO | Scheduled Service | Closed | N | CAROL | Administrator
2013-04-29 08:56 | 1-6696323989 | LOX588443 | L&M | Closed | Proposal to plug chiller 9 and chiller 10 | 2013-04-30 |  |  |  |  | 2013-05-01 08:56 |  | Custom Quote | Closed | Y | TOM | Johnson
2013-04-17 14:13 | 1-6662123802 | LOX583374 | L&M | Closed | Provide eddycurrent testing on all condenser and evaporator tubes on chillers #8, 9, and 10. Note: Head removal and tube cleaning provided by others. CH-8 m/n OTT4G2-ZBES s/n GACM117864 CH-9 m/n OTT4G2-ZBES s/n GACM127698 CH-10 m/n OTT4G2-ZBES s/n GACM127699 | 2013-04-23 |  |  |  |  | 2013-04-19 14:13 |  | Custom Quote | Closed | Y | TOM | Johnson
2013-02-28 13:06 | 1-6482766674 | LOX585576 | L&M | Closed | Rupture disk replacement Chiller 8 and two spare disks. 8 hours labor to include: Three Disks One Disk Holder | 2013-04-11 |  |  |  |  | 2013-03-02 13:06 |  | Custom Quote | Closed | Y | TOM | Johnson
2013-02-25 09:11 | 1-6465393059 | LOX585468 | L&M | Closed | Furnish qty-1 55 gallon container of York "K" oil | [5 empty] | 2013-02-27 09:11 |  | Custom Quote | Closed | Y | TOM | Stetson
2013-02-01 01:00 | 1-6247036719 |  | PSA | Closed | Preventive Maintenance | 2013-03-04 |  |  |  |  | 2013-01-03 10:51 | 1-2GEM8RO | Scheduled Service | Closed | N | CAROL | Administrator
2013-01-16 08:44 | 1-6308784998 | LOX583896 | L&M | Closed | Budgetary proposal to rebuild compressor on Chiller #8. m/n OTT4G2-ZBES s/n GACM117864 Lock out / tag out all energy sources Recover and store all refrigerant using plant recovery system Disconnect compressor coupling Disconnect all compressor piping Set up rigging and lower compressor to ground Record compressor thrust and runout readings Disassemble entire compressor and evaluate all parts Furnish and install new compressor bearings and gaskets Record compressor thrust and runout readings after rebuild Rig compressor onto chiller Reconnect all piping Pressure test system with nitrogen and leak test Check and adjust motor alignment as needed Reassemble compressor coupling Evacuate system and charge with recovered refrigerant Run chiller and check operation Provide all documentation Note: Pricing per chiller. 50,066.00 | 2013-01-31 |  |  |  |  | 2013-01-18 08:44 |  | Custom Quote | Closed | Y | TOM | Johnson
2012-12-01 01:00 | 1-6002646799 |  | PSA | Closed | Preventive Maintenance | 2013-03-02 |  |  |  |  | 2012-11-03 11:42 | 1-2GEM8RO | Scheduled Service | Closed | N | CAROL | Administrator
2012-11-19 08:58 | 1-6073656448 | LOX581421 | L&M | Closed | MATERIAL ONLY Furnish qty-1 55 gal. drum of York "K" oil | [5 empty] | 2012-11-21 08:58 |  | Custom Quote | Closed | Y | TOM | Johnson
2012-09-01 01:00 | 1-5587255578 |  | PSA | Closed | Preventive Maintenance | 2013-03-14 |  |  |  |  | 2012-08-03 13:43 | 1-2GEM8RO | Scheduled Service | Closed | N | CAROL | Administrator
2012-08-29 07:48 | 1-5710749030 | LDFS25135 | L&M | Closed | PARTS ORDER DuPont Experimental Station Absorber #2 m/n YPCST226-46-CXA s/n GADM248980 •Furnish and install qty-1 new absorber pump impeller. •Run unit and check operation. | [5 empty] | 2012-08-31 07:48 |  | Custom Quote | Closed | Y | TOM | Johnson
2012-08-02 10:09 | 1-5591819781 | LGGC16834 | L&M | Closed | Repair Absorber #2 Solution Pump. Furnish and install qty-1 new pump motor with repair kit. Furnish and install qty-1 new pump overload relay Furnish and install qty-1 new pump contactor. Start pump and check operation. | 2012-08-29 |  |  |  |  | 2012-08-04 10:09 |  | Custom Quote | Closed | Y | TOM | Williams
2012-08-01 01:00 | 1-5515764727 |  | PSA | Closed | Preventive Maintenance | 2012-08-02 |  |  |  |  | 2012-07-21 07:36 | 1-2GEM8RO | Scheduled Service | Closed | N | CAROL | Administrator
2012-07-30 16:44 | 1-5570855801 |  | L&M | Closed | ABSORBER PUMP DOWN | 2012-07-30 |  |  |  |  | 2012-08-01 16:47 |  | Labor & Material | Closed | Y | TOM | Johnson
2012-06-12 10:51 | 1-5326246850 |  | L&M | Cancelled | Take service call on Absorber #2 down. Have operators switch over to chiller start chiller #2. Start chiller and begin to check operation. Building had fire alarm and had to be evacuated. Upon return check out and log chiller #2 and check operation. Also check operation of absorbers #1,and #3. | [5 empty] | 2012-06-14 10:51 |  | Custom Quote | Created In Error | Y | TOM | Johnson
2012-06-12 10:08 | 1-5326338169 | LGGC16318 | L&M | Closed | Use PO LGGC16318 DuPont Experimental Station Wilmington, DE •Furnish and install Lithium Molybdate inhibitor in qty-4 absorption chillers as needed based on analysis results. | 2012-07-02 |  |  |  |  | 2012-06-14 10:08 |  | Custom Quote | Closed | Y | TOM | Johnson
2012-06-05 08:33 | 1-5291903176 | LOX574005 | L&M | Closed | Use PO # LOX574005 •Furnish qty-2 new purge transducers p/n 025-29907-002. | [5 empty] | 2012-06-07 08:33 |  | Custom Quote | Closed | Y | TOM | Johnson
2012-05-29 09:14 | 1-5249959211 |  | L&M | Cancelled | Service call to address problem with absorber #2 Quote needed from job before billing ACTIVITY MOVED TO SR#1-5326246850. | [5 empty] | 2012-05-31 09:25 |  | Labor & Material | Created In Error | Y | Tom | Johnson
2012-05-25 08:20 | 1-5238056088 | LGGC16094 | L&M | Closed | DuPont Experimental Station Absorber #3 m/n YPCST226-46-CXA s/n GADM233620 •Respond to service call on unit shutting down on “High first stage generator temperature”. •Run unit through de-crystallization procedure. •Apply external heat to liquefy stubborn areas. •Run unit and check operation. | 2012-05-07 |  |  |  |  | 2012-05-27 08:20 |  | Custom Quote | Closed | Y | Tom | Johnson
2012-05-07 12:25 | 1-5146711973 |  | L&M | Cancelled | DE-CRYSTALIZING ABSORBER #3 (Activity needs to be moved to SR#1-5238056088) then billed as quoted job. | [5 empty] | 2012-05-09 12:26 |  | Labor & Material | Created In Error | Y | Tom | Johnson
2012-05-01 01:00 | 1-4963268475 |  | PSA | Closed | Preventive Maintenance | 2012-05-29 |  |  |  |  | 2012-04-02 14:34 | 1-1EN3RF2 | Scheduled Service | Closed | N | CAROL | Administrator
2012-04-03 08:32 | 1-4972943318 | LGGC15615 | L&M | Closed | USE PO# LGGC15615 Chiller #10 Job Scope: Furnish and install qty-1 Norris Valve seal kit. •Lock out / Tag out all energy sources. •Furnish and install qty-1 valve O-ring kit for free cooling valve. •Pressurize and leak check new valve. •Clean up chiller. •Check operation. •Note: Refrigerant recovery and recharge performed by others. | 2012-04-24 |  |  |  |  | 2012-04-05 08:32 |  | Custom Quote | Closed | Y | Tom | Johnson
2012-04-03 08:27 | 1-4972942980 | LGGC15614 | L&M | Closed | Use PO#LGGC15614 Chiller #9 Job Scope: Furnish and install qty-1 Norris Valve seal kit. •Lock out / Tag out all energy sources. •Furnish and install qty-1 valve O-ring kit for free cooling valve. •Pressurize and leak check new valve. •Clean up chiller. •Check operation. •Note: Refrigerant recovery and recharge performed by others. | 2012-05-05 |  |  |  |  | 2012-04-05 08:27 |  | Custom Quote | Closed | Y | Tom | Johnson
2012-03-12 09:03 | 1-4856238148 | LGGC15395 | L&M | Closed | Use PO#LGGC15395 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 Norris Valve seal kit. •Lock out / Tag out all energy sources. •Furnish and install qty-1 valve O-ring kit. •Pressurize and leak check new valve. •Check operation. | 2012-04-04 |  |  |  |  | 2012-03-14 09:03 |  | Custom Quote | Closed | Y | TOM | Johnson
2012-03-09 16:28 | 1-4849659201 | LGGC15435 | L&M | Closed | BLDG 336 CHILLER IN ALARM | 2012-03-10 |  |  |  |  | 2012-03-11 16:30 |  | Labor & Material | Closed | Y | CAROL | Johnson
2012-02-29 13:13 | 1-4794930239 | LGGC14985 | L&M | Closed | THIS IS 2 OF 2 ( PARTIAL BALANCE ) Original SR 1-4712912261 has been billed for $12,000.00 USE PO# LGGC14985 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. •Lock out / Tag out all energy sources. •Recover and weigh entire refrigerant charge using plant recovery system. •Disassemble compressor coupling. •Remove and replace compressor shaft seal. •Leak test entire chiller with nitrogen. •Evacuate chiller and perform vacuum hold test. •Check coupling alignment using laser alignment tool. •Reassemble compressor coupling. •Charge chiller with recovered refrigerant. •Furnish and install 20 gallons of new compressor oil. •Run chiller and check operation. | 2012-03-21 |  |  |  |  | 2012-03-02 13:13 |  | Custom Quote | Closed | Y | Tom | Johnson
2012-02-29 12:13 | 1-4793406009 | LGGC14985 | L&M | Cancelled | PART TWO OF JOB. WILL NEED TO TURN INTO QUOTE USE PO# LGGC14985 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. •Lock out / Tag out all energy sources. •Recover and weigh entire refrigerant charge using plant recovery system. •Disassemble compressor coupling. •Remove and replace compressor shaft seal. •Leak test entire chiller with nitrogen. •Evacuate chiller and perform vacuum hold test. •Check coupling alignment using laser alignment tool. •Reassemble compressor coupling. •Charge chiller with recovered refrigerant. •Furnish and install 20 gallons of new compressor oil. •Run chiller and check operation. | [5 empty] | 2012-03-02 12:16 |  | Custom Quote | Created In Error | Y | TOM | Hegarty
2012-02-14 12:01 | 1-4712912261 | LGGC14985 | L&M | Closed | USE PO# LGGC14985 DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. Lock out / Tag out all energy sources. Recover and weigh entire refrigerant charge using plant recovery system. Disassemble compressor coupling. Remove and replace compressor shaft seal. Leak test entire chiller with nitrogen. Evacuate chiller and perform vacuum hold test. Check coupling alignment using laser alignment tool. Reassemble compressor coupling. Charge chiller with recovered refrigerant. Furnish and install 20 gallons of new compressor oil. Run chiller and check operation. | 2012-02-25 |  |  |  |  | 2012-02-16 12:01 |  | Custom Quote | Closed | Y | TOM | Johnson
2012-02-07 14:28 | 1-4673843608 |  | L&M | Cancelled | DuPont Experimental Station Chiller #8 m/n LKC-73 Job Scope: Furnish and install qty-1 new compressor shaft seal. •Lock out / Tag out all energy sources. •Recover and weigh entire refrigerant charge using plant recovery system. •Disassemble compressor coupling. •Remove and replace compressor shaft seal. •Leak test entire chiller with nitrogen. •Evacuate chiller and perform vacuum hold test. •Check coupling alignment using laser alignment tool. •Reassemble compressor coupling. •Charge chiller with recovered refrigerant. •Run chiller and check operation. | [5 empty] | 2012-02-09 14:29 |  | Custom Quote | Created In Error | Y | TOM | Johnson
2012-02-01 01:00 | 1-4458302276 |  | PSA | Closed | Preventive Maintenance | 2012-05-09 |  |  |  |  | 2012-01-03 07:45 | 1-1EN3RF2 | Scheduled Service | Closed | N | CAROL | Administrator
2012-01-22 15:18 | 1-4574444162 | LGGC14883 | L&M | Closed | DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 Job Scope: •Premium time for work performed by Mike Ianovale and Joe Fisher on Saturday 1-7-12. | 2012-01-07 |  |  |  |  | 2012-01-24 15:18 |  | Custom Quote | Closed | Y | TOM | Johnson
2012-01-20 15:02 | 1-4566677889 |  | L&M | Cancelled | PREMIUM TIME COVERAGE NEEDED FOR EQUIPMENT REPAIR weekend of 1/7/2012. premium time to start and test chiller#7 for the hot alignment check | [5 empty] | 2012-01-22 15:02 |  | Custom Quote | Created In Error | Y | CAROL | Johnson
2012-01-17 11:13 | 1-4544978844 | LGGC14775 | L&M | Closed | use po# LGGC14775 DuPont Experimental Station Chiller #7. •Furnish and install qty-1 new additional bursting disk relief indicators for refrigerant relief valves. •Isolate, lock out and tag out valves as required. •Disassemble assembly and clean all gasket surfaces. •Furnish and install new bursting disk and gaskets. •Leak test assembly. | 2012-04-30 |  |  |  |  | 2012-01-19 11:13 |  | Custom Quote | Closed | Y | TOM | Johnson
2012-01-09 09:03 | 1-4491902342 |  | L&M | Cancelled | PREMIUM TIME COVERAGE NEEDED FOR EQUIPMENT REPAIR ** PAUL NEEDS TO CONVERT TO QUOTED PRICE ** Cancelled. | [5 empty] | 2012-01-11 09:04 |  | Labor & Material | Created In Error | Y | Tom | Johnson
2011-12-05 10:15 | 1-4311150501 | LGGC14480 | L&M | Closed | USE PO# DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 •Furnish qty-1 new seal end compressor bearing. •Furnish qty-1 new Pump end compressor bearing. •Furnish qty-1 new reverse thrust bearing. | 2011-12-14 |  |  |  |  | 2011-12-07 10:15 |  | Custom Quote | Closed | Y | Tom | Johnson
2011-12-01 01:00 | 1-4191187406 |  | PSA | Closed | Preventive Maintenance | 2012-01-10 |  |  |  |  | 2011-11-12 07:33 | 1-1EN3RF2 | Scheduled Service | Closed | N | Tom | Administrator
2011-12-01 01:00 | 1-4138658401 |  | PSA | Closed | Preventive Maintenance | 2012-05-10 |  |  |  |  | 2011-11-02 12:43 | 1-1EN3RF2 | PSA Repair | Closed | N | TOM | Administrator
2011-11-29 15:15 | 1-4276984327 | LGGC14336 | L&M | Closed | USE PO# LGGC14336 DuPont Experimental Station Chiller #7. •Furnish and install qty-5 new bursting disk relief indicators for refrigerant relief valves. oQty-2 disks on Chiller #7 Evaporator oQty-2 disks on refrigerant recovery receiver. oQty-1 disk on refrigerant recovery unit. •Isolate, lock out and tag out valves as required. •Disassemble assemblies and clean all gasket surfaces. •Furnish and install new bursting disks and gaskets. •Leak test each assembly. | 2012-02-04 |  |  |  |  | 2011-12-01 15:15 |  | Custom Quote | Closed | Y | TOM | Johnson
2011-11-29 13:31 | 1-4276011500 | LGGC14336 | L&M | Closed | USE PO#LGGC14336 DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 Job Scope: Perform compressor bearing inspection and coupling alignment on qty-1 York OM chiller. •Lock out / Tag out chiller. •Transfer refrigerant charge to storage vessel using plant transfer system. •Disassemble compressor coupling. •Check and record compressor shaft runout and thrust readings. •Drain oil from compressor. •Dissemble compressor oil sump cover and oil pump. •Remove and inspect front compressor bearing. •Disassemble compressor shaft seal. •Remove and inspect rear compressor bearing. •Reassemble both compressor bearing assemblies with new gaskets. •Furnish and install new compressor shaft seal. •Recheck compressor runout and thrust readings. •Install new compressor oil and filters. (Supplied by customer) •Pressurize compressor with nitrogen and leak test. •Disassemble motor to gearbox coupling. •Check and record alignment of both couplings using laser tool and dial indicators. •Adjust alignments if needed to bring within factory specs. •Perform coupling maintenance. •Reassemble both couplings. •Evacuate system and perform vacuum hold test. •Recharge chiller with recovered refrigerant. •Check chiller operation. •Provide all documentation. | 2011-12-23 |  |  |  |  | 2011-12-01 13:31 |  | Custom Quote | Closed | Y | TOM | Johnson
2011-11-29 13:24 | 1-4276011474 | LGGC14377 | L&M | Closed | USE PO# LGGC14377 DuPont Experimental Station Absorbers. #1 m/n YPCST22G46CXA s/n GLCM157836. #2 m/n YPCST22G46CXA s/n GBDM248980. #3 m/n YPCST22G46CXA s/n GADM233620. #4 m/n YPCST22G46CXA s/n GNCM9423001. Job Scope: Furnish and install new non-fragmenting type bursting disks and disk holders on each chiller. (Qty-2 per chiller. Total of qty-8). •Lock out / Tag out chiller. •Remove old carbon type disks and gaskets. •Re-fabricate piping as needed to accept new disk holders. •Furnish and install new disks and disk holders. •Pressurize and leak check around new bursting disks. •Provide all documentation. | 2012-02-11 |  |  |  |  | 2011-12-01 13:24 |  | Custom Quote | Closed | Y | TOM | Johnson
2011-11-03 15:35 | 1-4160612327 | LGGC14144 | L&M | Cancelled | USE PO# LGGC14144 DuPont Experimental Station Chiller #7 m/n OM5000 s/n MRP626904 Job Scope: Perform motor, gearbox, and compressor coupling alignment. •Lock out / Tag out chiller •Disassemble motor to gearbox and gearbox to compressor couplings. •Check and record alignment of both couplings using laser tool and dial indicators. •Adjust alignments if needed to bring within factory specs. •Perform coupling maintenance. •Reassemble both couplings. •Check chiller operation. •Provide all documentation. | [5 empty] | 2011-11-05 15:35 |  | Custom Quote | Customer Cancelled | Y | TOM | Johnson
2011-11-03 13:19 | 1-4160013757 | LGGC14145 | L&M | Closed | USE PO# LGGC14145 DuPont Experimental Station Absorber #2 m/n YPCST22G46CXA s/n GBDM248980 Job Scope: Troubleshoot low refrigerant temperature alarm. •Lock out / Tag out chiller •Check refrigerant flow to spray headers. •Change refrigerant pump. (Pump supplied by customer) •Check chiller operation. •Provide all documentation. | 2011-11-01 |  |  |  |  | 2011-11-05 13:19 |  | Custom Quote | Closed | Y | TOM | Johnson
2011-09-22 11:16 | 1-3896106608 | LOX559651 | Material Only | Closed | Material Order for (1) "55 Gallon Drum of K-Oil (011 00534 000) and (1) "5 Gallon drum of K-Oil (011 00533 000). | [5 empty] | 2011-09-24 11:16 |  | Material Only Quote | Closed | Y | Diane | Johnson
2011-09-13 09:41 | 1-3832679073 | LGGC12820 | L&M | Closed | CHILLER #3 DOWN | 2011-09-13 |  |  |  |  | 2011-09-15 09:44 |  | Labor & Material | Closed | Y | Tom | Johnson
2011-08-10 09:37 | 1-3614184300 | LGGC12820 | L&M | Closed | POWER FAILURE - CHILLER DOWN | 2011-08-10 |  |  |  |  | 2011-08-12 09:39 |  | Labor & Material | Closed | Y | Tom | Johnson
2011-08-01 01:00 | 1-3314236480 |  | PSA | Closed | Preventive Maintenance | 2011-11-04 |  |  |  |  | 2011-07-03 07:51 | 1-1EN3RF2 | Scheduled Service | Closed | N | CAROL | Administrator
2011-07-13 08:51 | 1-3395663956 | LMCH10247 | L&M | Closed | Use PO# LMCH10247 DuPont Experimental Station Absorption Chillers #3 and #4 Absorber #3 m/n YPCST22G46CX s/n GADM233620 Absorber #4 m/n YPCST22G46CX s/n GNCM9423001 •Furnish and install Adva-Guard 591 chemical inhibitor for qty-2 York Absorption Chillers based on solution analysis results.. •Chiller #3…… 2.7 lbs. •Chiller #4…….2.82 lbs. | 2011-07-28 |  |  |  |  | 2011-07-15 08:51 |  | Custom Quote | Closed | Y | CAROL | Johnson
2011-07-06 14:34 | 1-3350806150 | LMCH10237 | L&M | Closed | TROUBLESHOOT AND REPAIR THE #10 CHILLER AT E315 | 2011-07-06 |  |  |  |  | 2011-07-08 14:37 |  | Labor & Material | Closed | Y | TOM | Johnson
2011-07-01 01:00 | 1-3073406829 |  | PSA | Closed | Preventive Maintenance | 2011-07-22 |  |  |  |  | 2011-06-04 10:40 | 1-1EN3RF2 | Scheduled Service | Closed | N | CAROL | Administrator
2011-05-12 11:09 | 1-2913970345 |  | PSA | Closed | ABSORBER PM'S | 2011-05-12 |  | 2670593 | YPC-ST-22G-46-C-X-A | GNCM94230017 | 2011-05-14 11:17 | 1-EOSB6J | Scheduled Maintenance | Closed | N | Tom | Johnson
2011-05-01 01:00 | 1-2635588274 |  | PSA | Closed | Preventive Maintenance | 2011-06-01 |  |  |  |  | 2011-04-02 09:39 | 1-EOSB6J | Scheduled Service | Closed | N | CAROL | Administrator
2011-04-14 12:17 | 1-2720351788 | LGGC10244 | L&M | Closed | Dupont Experimental Station Building 336. York YCAS190 Chiller. •Furnish and install qty-1 new condenser fan motor, fan blade, and blade mounting hardware. (Fan #7). •Furnish and install qty-1 new suction temperature sensor. •Furnish and install qty-1 new oil pressure transducer. •Start chiller and check operation. •Note: All work to be performed on a Saturday. NOT DONE | 2011-04-30 |  |  |  |  | 2011-04-16 12:17 |  | Custom Quote | Closed | Y | CAROL | Johnson
2011-03-30 11:09 | 1-2627851260 |  | PSA | Closed | PURGE PUMP MAINT. |  |  | 2675068 |  |  | 2011-04-01 11:18 | 1-EOSB6J | Scheduled Maintenance | Closed | N | CAROL | Johnson
2011-03-16 16:34 | 1-2548420121 | LGGC9754 | L&M | Closed | E336 CHILLER SERVICE CALL..... (waiting on parts to hit job) | 2011-03-19 |  |  |  |  | 2011-03-18 16:36 |  | Labor & Material | Closed | Y | CAROL | Johnson
2011-02-16 15:56 | 1-2382254821 | LGGC8974 | L&M | Closed | Use PO # LGGC8974 DuPont Experimental Station Chiller #8. m/n OTT4G2-2BES s/n GACM117864 Furnish and install qty-1 new oil pump shaft seal kit on chiller #8. Remove and weigh refrigerant charge from chiller using plant recovery / transfer system. Disassemble oil pump and install new pump shaft seal kit. Pressurize chiller with nitrogen and leak test. Evacuate and recharge chiller with recovered refrigerant. Check oil pump operation. | 2011-02-25 |  |  |  |  | 2011-02-18 15:56 |  | Custom Quote | Closed | Y | CAROL | Johnson
2011-02-04 14:57 | 1-2322219561 | LGGC8619 | L&M | Closed | DuPont Experimental Station York Chiller #7. USE PO# LGGC8619 Furnish and install qty-1 new Monitech LCD display monitor on chiller control panel. Note: The Monitech display is an aftermarket display which replaces the tube only and utilizes the existing panel interface. ( No programming required). The original display is no longer available. | 2011-02-22 |  |  |  |  | 2011-02-06 14:57 |  | Custom Quote | Closed | Y | CAROL | Johnson
2011-02-01 01:00 | 1-2145850208 |  | PSA | Closed | Preventive Maintenance | 2011-05-13 |  |  |  |  | 2011-01-03 11:00 | 1-EOSB6J | Scheduled Service | Closed | N | CAROL | Administrator
2011-01-18 15:17 | 1-2224249835 | LOX548915 | Material Only | Closed | MATERIAL ORDER FOR (6) OIL FILTERS FOR YORK CHILLERS. QUOTED AMOUNT $219.90. | [5 empty] | 2011-01-20 15:22 |  | Material Only Quote | Closed | Y | TOM | Johnson
2010-12-27 08:06 | 1-2110929898 | CAROL BAFFONE | L&M | Closed | •Furnish and install qty-10 new gaskets on bursting disk relief indicators for refrigerant relief valves. •Isolate, lock out and tag out valves as required. •Disassemble assemblies and clean all gasket surfaces. •Furnish and install new gaskets. •Leak test each assembly. | 2010-12-28 |  |  |  |  | 2010-12-29 08:06 |  | Custom Quote | Closed | Y | CAROL | Johnson
2010-12-18 09:10 | 1-2083406911 |  | L&M | Closed | YCAS190 chiller was experiencing a low temperature alarm. | 2010-12-18 |  |  |  |  | 2010-12-20 09:12 |  | Labor & Material | Closed | Y | CAROL | Johnson
2010-12-08 09:56 | 1-2031869374 | LGGC7651 | L&M | Closed | Provide Eddy current testing on all condenser and evaporator tubes on Chiller #7. Furnish detailed report of tube condition in hard copy and PDF format. Note: Condenser and evaporator heads must be removed and all tubes must be brush cleaned before testing can begin. (Performed by others). | 2010-12-20 |  |  |  |  | 2010-12-10 09:56 |  | Custom Quote | Closed | Y | CAROL | Johnson
2010-12-07 14:40 | 1-2027396439 |  | L&M | Cancelled | EDDY CURRENT TESTING - ACTIVITY TO BE MOVED AFTER COMPLETION OF QUOTE. | [5 empty] | 2010-12-09 14:41 |  | Labor & Material | Created In Error | Y | TOM | Johnson
2010-12-01 01:00 | 1-1828518509 |  | PSA | Closed | Preventive Maintenance | 2010-11-15 |  |  |  |  | 2010-11-02 12:26 | 1-EOSB6J | Scheduled Service | Closed | N | CAROL | Administrator
2010-11-15 21:56 | 1-1907409794 |  | PSA | Closed | ABSORBER SHUTDOWN | 2010-11-26 |  | 2675067 |  |  | 2010-11-17 21:59 | 1-EOSB6J | Scheduled Maintenance | Closed | N | TOM | Johnson
2010-10-05 10:19 | 1-1693076316 | LMCH10247 | Material Only | Closed | MATERIAL QUOTE FOR INHIBITOR. | [5 empty] | 2010-10-07 10:35 |  | Material Only Quote | Closed | Y | TOM | Johnson
2010-09-23 15:50 | 1-1617871854 | LDFS25135 | L&M | Closed | Furnish and install qty-1 new keypad for Absorption chiller #1. | 2010-09-27 |  |  |  |  | 2010-09-25 15:50 |  | Custom Quote | Closed | Y | CAROL | Johnson
2010-08-14 10:31 | 1-1384543671 |  | L&M | Closed | REPAIRS TO RTU BLDING 336 (WEEKEND ACCESS) | 2010-08-14 |  |  |  |  | 2010-08-16 10:32 |  | Labor & Material | Closed | Y | CAROL | Johnson
2010-08-09 20:17 | 1-1357550573 |  | PSA | Closed | Preventive Maintenance | 2010-09-21 |  |  |  |  | 2010-08-11 20:17 | 1-EOSB6J | Scheduled Service | Closed | N | TOM | Administrator
2010-08-09 16:43 | 1-1356202728 |  | PSA | Closed | OPERATIONAL SSV'S | 2010-09-30 |  | 2675067 |  |  | 2010-08-11 16:44 | 1-EOSB6J | Scheduled Maintenance | Closed | N | TOM | Johnson
2010-08-04 14:20 | 1-1329193316 | LGGC4301 | L&M | Closed | ABSORBER #2 DOWN ON LOW REFRIGERANT | 2010-08-05 |  |  |  |  | 2010-08-06 14:26 |  | Labor & Material | Closed | Y | Tom | Johnson
2010-07-30 14:48 | 1-1297135051 | LGGC4301 | L&M | Closed | ABS 2 Leak Repairs | 2010-08-03 |  |  |  |  | 2010-08-01 14:50 |  | Labor & Material | Closed | Y | TOM | Johnson
2010-07-23 10:18 | 1-1249898436 |  | L&M | Closed | REPAIRS TO RTU IN BLDG 336. FIRST CALL - SERVICE CALL ON SATURDAY. | 2010-07-24 |  |  |  |  | 2010-07-25 10:23 |  | Labor & Material | Closed | Y | PAUL | Johnson
2010-07-12 11:11 | 1-1189019721 | LGGC4301 | L&M | Closed | PARTIAL BILLING - PURGE UNIT ON #2 CHILLER MALFUNCTIONING. | 2010-07-30 |  |  |  |  | 2010-07-14 11:19 |  | Labor & Material | Closed | Y | Tom | Johnson
2010-06-14 08:53 | 1-1021703411 | LGGC4301 | PSA | Closed | CHILLER #3 OFFLINE | 2010-07-06 |  | 2670592 |  |  | 2010-06-16 08:55 | 1-EOSB6J | PSA Repair | Closed | N | TOM | Johnson
2010-06-09 09:15 | 1-996861621 |  | L&M | Closed | Perform seasonal maintenance on qty-1 YCAS0190 air-cooled chiller. Clean all condenser coils with pressure washer. Change compressor oil filter. Leak check entire chiller.Perform oil and refrigerant analysis. Check all condenser fan motors and blades. Check all chiller safeties and controls. Megger test compressor motor. Check compressor starter and tighten all connections. Start chiller and check operation. Note: All work to be performed on overtime. | 2010-06-12 |  |  |  |  | 2010-06-11 09:15 |  | Custom Quote | Closed | Y | TOM | Johnson
2010-06-01 09:25 | 1-951443420 |  | PSA | Closed | PM ON ABSORBERS | 2011-06-09 |  | 2675067 |  |  | 2010-06-03 09:39 | 1-EOSB6J | Scheduled Maintenance | Closed | N | TOM | Johnson
2010-05-26 08:46 | 1-904072214 | LGGC24TS | L&M | Closed | FINISH AND INSTALL (1) NEW LOW REFRIGERANT TEMP SWITCH. | 2010-05-27 |  |  |  |  | 2010-05-28 08:46 |  | Custom Quote | Closed | Y | TOM | Johnson
2010-05-13 08:14 | 1-832516755 |  | PSA | Closed | BASIC SEASONAL MAINT. | 2010-05-28 |  | 2675067 |  |  | 2010-05-15 08:17 | ENTL:92607131-28091 | Scheduled Maintenance | Closed | N | TOM | Johnson
2010-05-01 01:00 | 1-672193722 |  | PSA | Closed | Preventive Maintenance | 2010-08-09 |  |  |  |  | 2010-04-16 07:57 | ENTL:92607131-28090 | Scheduled Service | Closed | N | TOM | Administrator