## Slide 1: Types of Pumps
UA Pumps
CH 2 Section 2
Learning Outcome 3+4

## Slide 4: Closed Loop Systems
Key concepts
Are not exposed to atmosphere
Are under pressure even without fluid flow
When the system is in a Static Condition (no flow), pressure on both sides of the pump are the same
This is known as Static Head Negation

## Slide 7: Closed Loop Systems
Fig 2-27
What is the pressure at gauge 1?
60ft x .433 psi/ft = 25.98 psi or 26 psi
What is the pressure at gauge 2?
See how it is the same?
This is known as Static Head Negation

## Slide 8: Closed Loop Systems
In the closed system, the total of the changes in pressure on the pump gauges is equal to the additional head developed under flow conditions due to friction losses within the system
In a closed system Delta P represents the increase in head generated by the pump in order to overcome the resistance (or pressure drop) throughout the entire system due to friction loss

## Slide 11: Total Dynamic Head
The Total Dynamic Head is a direct representation of the performance of the pump at a specific flow rate and is a very useful tool during start-up, testing and balancing and in troubleshooting pump performance

## Slide 12: Closed Loop Systems
Learning Objectives Completed
  Reference provided diagrams IPT Pumps Fig-2-27 (Closed System) and explain concepts, Static Head Negation, Delta P, System Friction Loss, Total Dynamic Head
  Quick review Closed Loop Systems
  Theory
  Vocabulary

## Slide 14: Pump Curves
As total head increases, flow rate decreases
Conversely, as the total head becomes lower, the flow rate increases
The discharge rate of centrifugal pumps will vary according to the amount of system pressure being pumped against (Delta P)
This relationship of flow to system pressure is described graphically for each individual pump through a diagram called a pump curve

## Slide 16: Centrifugal Pump Curves
May be used to measure pump performance
They can show shut-off head
Determine Impeller Size
Show system flow at other than prevailing conditions
Determine pump horsepower and efficiency

## Slide 25: Changing Performance of a Centrifugal Pump
Change the rotational speed (RPM)
Change the diameter of the impeller
Change the style of the impeller

## Slide 28: Pumping Performance Options
Multi-Speed Motor
Parallel Pumping
  Each pump produces one-half of the total flow at the total system head
Series Pumping
  Each pump supplies the full design flow rate at one-half of the required design head

## Slide 31
GPM
Ft Hd
Pump A
Pump A + B
System Curve
Parallel Pumping Curve

## Slide 34
Ft Hd
GPM
The pump curves for two identical centrifugal pumps connected in series
Point of Operation
Pump A + B
Pump A
System
Curve

## Slide 37: Pumping Performance Options
Variable Volume Pumping
  Pump flow changes directly as a function of pump speed
  Pump head changes as a squared function of the pump speed change
Pump Primary / Secondary Pumping
  When two circuits are inter-connected, flow in one will not cause flow in the other if the pressure drop in the piping common to both is eliminated

## Slide 39
Pump Performance At Various Speeds

## Slide 40
Pumping Horsepower At Various Speeds

## Slide 44: Pump Curve
Learning Objectives Completed
  Demonstrate how to chart and interpret a pump curve and system curve
  Explain relationship between delta P and flow for a centrifugal pump.
  Explain three ways a centrifugal pump can be altered to achieve real world capacity
  Quick review Pump/ System curve and Balancing
  Theory
  Vocabulary

## Slide 46: Materials Used In Pump Construction for HVAC and General Pumping
Bronze Fitted Pumps
  Cast iron pump body or volute
  Steel shaft
  Bronze impellor
All Bronze Pumps
  All wetted parts made of bronze or other non ferrous materials
Stainless Steel Pumps
  Volutes, impellors, and shafts of stainless steel

## Slide 47
P 28

## Slide 48: Pump Prime Movers
Steam Turbine
Diesel Engine
Electric Motor
  Open Drip Proof (ODP)
  Totally Enclosed Fan Cooled (TEFC)
  Explosion Proof

## Slide 55: Pump Bodies
In-line
Close-coupled, in-line
End suction, close-coupled, foot-mounted
End suction, base-mounted
Double suction, vertical split case, base-mounted
Double suction, horizontal split case, base-mounted
Vertical, multi-stage
Vertical, turbine

## Slide 57: In-line
Hydronic heating and cooling
Hot water recirculation
Heat recovery
Solar thermal heating
Heat pumps

## Slide 67: Close coupled, In-line
Water supply and boosting
Heating, air conditioning and condenser water systems
Liquid transfer and general service in commercial, industrial and agricultural applications

## Slide 72: End Suction, Close Coupled, Foot Mount
Cooling Towers
HVAC
General Purpose

## Slide 78: End Suction, Base Mounted
Heating Systems
Chilled Water
Cooling Tower
Industrial
General Purpose

## Slide 80: Centrifugal Styles and Applications
Learning Objectives Completed
  Explain 6 different styles and applications of centrifugal pumps IPT Pumps Fig 2-29
  Quick review Centrifugal Style and Applications
  Theory
  Vocabulary

## Slide 82: PUMP COMPONENTS

## Slide 83: ‘TRUE’ Back Pull-out Design
Remove back of pump without disturbing:
  system piping
  motor alignment
Reduced downtime
Lower cost

## Slide 84: SELF FLUSHING SEAL
Provides Maximum:
Internal seal face lubrication
Heat dissipation
Debris removal
Passes 2 to 3 times more fluid over the
seal face than externally flushed seal

## Slide 85: FOOT MOUNTED VOLUTE
integrally cast foot
maintains alignment
eliminates deflection

## Slide 86: ANSI/OSHA Coupling Guard
Standard on 1510
Highest level of safety
Reduces potential for liability

## Slide 87
SHORT SHAFT OVERHANG
Promotes reduced:
shaft deflection
bearing wear
seal wear
Casing wear ring not required

## Slide 90: Double Suction, Vertical Split Case, Base Mounted
Hydronic Heating and Cooling Systems
Condenser Water
Cooling Towers
Refrigeration
General Service

## Slide 95: Double Suction, Horizontal Split Case, Base Mounted
Hydronic Heating and Cooling Systems
General Service
Industrial
Fire Pumps

## Slide 101: Vertical, Multistage
General Service
Pressure Boosting
Chilled Water Circulation
Boiler Feed
Condensate Return
Pressure Wash
Cooling Tower Circulation

## Slide 105: Vertical, Turbine
Fluid Transfer
Petroleum Tank Farm
Booster Service
Fuel Loading
Cooling Tower
Industrial Process
Agriculture Irrigation
Water Treatment
Municipal Water Supply

## Slide 110: Fixture Pumps
Water closets
Urinals
Laundry trays

## Slide 113: Pumps Still Out There?
Drinking fountain pump
Pump Jack
  Driven by windmill, pump jack, or hand
Cistern pump

## Slide 116: Turbine Pumps
Turbine pumps are available in single, two, three or four stage models
They are generally used for low flow applications involving high pressures such as boiler feed water systems, etc
Available in heads up to 5400 ft. and in capacities up to 150 gpm

## Slide 120: Turbine Pumps
Learning Objectives Completed
  Define and describe different types of turbine pumps
  Quick review Vacuum Pump
  Theory
  Vocabulary

## Slide 122: Vacuum Pumps
A vacuum pump is used to exhaust air from a vessel or system to create a pressure condition below that of atmosphere
Vacuum pumps are used to evacuate refrigeration systems

## Slide 124: Vacuum Pumps
Learning Objectives Completed
  Explain the operation and uses of the vacuum pump
  Quick review Vacuum Pump
  Theory
  Vocabulary

## Slide 126: Hydrostatic Test Pumps
Hydrostatic test pumps are used to test piping systems installed by pipe trades journeyman
Hand operated hydrostatic test pumps can be used for testing residential water lines and pressure testing small pressure tanks, sprinkler, hydronic heating and solar piping systems

## Slide 130: Hydrostatic Test Pumps
Learning Objectives Completed
  Explain the operation and uses of the vacuum pump
  Quick review Vacuum Pump
  Theory
  Vocabulary

## Slide 132: Checkpoint 2
Assignment 2
Checkpoint 1 through Checkpoint 2
Pages 24 through 35
Learning Outcome 3 and 4 Completed
  Examine pressure relationships in closed systems generated by a centrifugal pump to determine and adjust fluid capacity
  Articulate major pump classifications, and then compare/contrast operational theory with common applications
Review Questions