## Slide 1: ELECTRONICS / VFD
Electronic Controls
FOR
HVAC
HVAC
Notes: 1

## Slide 2: VARIABLE FREQUENCY DRIVES
INTRODUCTION TO VFD BASICS
OVERVIEW OF POWER SIDE COMPONENTS
FUNCTIONS OF EACH COMPONENT DISCUSSED

## Slide 3: 3 PHASE RECTIFIER
Made-up of six fast-acting, high voltage diodes.

## Slide 4: 3 PHASE RECTIFIER
As the positive half of an AC sine wave enters the rectifier, it will conduct through the respective anode on that phase, and add its potential to the positive bus...

## Slide 5: 3 PHASE RECTIFIER

## Slide 6: 3 PHASE RECTIFIER

## Slide 7: 3 PHASE RECTIFIER
The negative half of the sine wave will have the exact opposite effect, conducting its potential through the respective cathode on that phase, adding to the negative bus...

## Slide 8: 3 PHASE RECTIFIER

## Slide 9: 3 PHASE RECTIFIER

## Slide 10
DC LINE REACTOR
> HELPS TO SMOOTHE CURRENT WAVEFORM

## Slide 11: DC LINE REACTOR
Consists of an iron-core inductor, designed and sized to reduce variations in current wave from.

## Slide 12: DC LINE REACTOR
Vary in sizes according to Kw, some reactors can get quite large and heavy.

## Slide 13: DC LINE REACTOR

## Slide 14
ELECTROLYTIC CAPACITORS
> CONVERT PULSATING DC INTO CONSTANT DC

## Slide 15: CAPACITORS
Electrolytic capacitors are polarized, which means they are sensitive to bus polarity.

## Slide 16: CAPACITORS
Their maximum voltage rating is 400 volts DC, due to the properties of the dielectric material separating the plates.

## Slide 17: CAPACITORS
The capacitor would then resemble this image in theory. Small pulses added, and a steady stream as an output.

## Slide 18: CAPACITORS
Remember!!!!! Be 100% SURE of the polarity of DC capacitors before energizing, OR ELSE…...

## Slide 19
BLEED RESISTORS
> BLEED DOWN VOLTAGE HELD IN CAPACITORS
WHEN LINE VOLTAGE IS REMOVED
> ACT AS VOLTAGE DIVIDER FOR CAPACITORS

## Slide 20: BLEED RESISTORS
Complete the necessary path to help dissipate the residual voltage held by the charged plates when power is removed.

## Slide 21: BLEED RESISTORS
They also insure that the voltage drop across the capacitors will be exactly the same.
(Remember the 400 VDC rating)

## Slide 22: BLEED RESISTORS
If one of the resistors should open, the voltage will be applied on only one cap.

## Slide 23
SOFT-START RESISTORS

## Slide 24: SOFT START RESISTOR
What is the resistance of a discharged capacitor?
A discharged capacitor has NO resistance, this is the reason why the needle of an analog meter will jump to 0 ohm when first connected.

## Slide 25: SOFT START RESISTOR
As demonstrated, an infinite amount of current will be available for the capacitors to charge to their full potential, which means any fuse or circuit breaker ahead of the caps will definitely open due to this unlimited surge.

## Slide 26: SOFT START RESISTOR
How can we slow down this inrush of current to the capacitors?
A resistance must be added in series with the capacitors. The size of this resistor will determine the charging time and the available current to the caps.

## Slide 27: SOFT START RESISTOR
Can the soft start resistor be located in series with the caps at this location to slow down the charging current?

## Slide 28: SOFT START RESISTOR
No, because it would slow down the charging and discharging effect of the capacitors.

## Slide 29: SOFT START RESISTOR
The resistor needs to be on the DC bus, since the voltage is always constant.

## Slide 30: SOFT START RELAY
It is more economical to use a three pole contactor and wire its contacts in parallel, rather than use a huge single pole contactor.

## Slide 31: SOFT START RELAY
A transistor may also be used to bypass the resistor.

## Slide 32
DC FUSE
> PROTECTS INVERTOR SECTION AGAINST
> USUALLY FAST ACTING FUSE
HIGH CURRENTS

## Slide 33: DC FUSE
Fast acting fuse, usually bolt-on type on 15 Hp drives and larger. A blown DC fuse most likely means serious and costly inverter problems.

## Slide 34
HALL-EFFECT
> MONITORS LOAD CURRENT AT DC BUS
CURRENT TRANSFORMER

## Slide 35
THREE PHASE INVERTOR
> PROVIDES PWM WAVEFORM TO LOAD
> FAST-FIRING IGBT TECHNOLOGY

## Slide 36: Solid-State Switches
Diode
SCR
GTO
Bipolar transistor & Darlington
IGBT
Notes: 21

## Slide 37: Diode
Notes: 23

## Slide 38: Diode
Allows current to flow only in one direction.
The switching occurs at low voltages.
Notes: 24

## Slide 39: Diode Used In
Diode bridge rectifiers.
Circuits that automatically control drive currents and voltages.
Notes: 25

## Slide 40: IGBT (Isolated Gate Bipolar Transistor)
Notes: 36

## Slide 41: IGBT (Isolated Gate Bipolar Transistor)
Easy to turn on.
Easy to turn off.
Very fast.
Rugged.
Notes: 37

## Slide 42: IGBT (Isolated Gate Bipolar Transistor) Used In
PWM inverters
  high frequency
  selectable frequency
  low frequency
  dynamically controlled frequency
Notes: 38

## Slide 43: The Inverter Section
Notes: 13

## Slide 44: Step 1
Notes: 14

## Slide 45: Step 2
Notes: 15

## Slide 46: Step 3
Notes: 16

## Slide 47: Step 4
Notes: 17

## Slide 48: Step 5
Notes: 18

## Slide 49: Step 6
Notes: 19

## Slide 50: The Amount of On Time Determines the Average Voltage
Notes: 64

## Slide 51: PWM Drive Output Waveform
Notes: 76

## Slide 52: PWM Drive Output Waveform
Notes: 76

## Slide 53: PWM Drive Output Waveform
Notes: 76

## Slide 54: Situations to avoid
Notes: 96

## Slide 55: Non-Interlocked Output Disconnect
Notes: 97

## Slide 56: Output Power Factor Capacitors
Notes: 98

## Slide 57: Isolation Transformer Primary Disconnect (without secondary disconnect)
Notes: 99

## Slide 58: Input Power Factor Correction with Isolation Transformer
Notes: 100

## Slide 59: POOR WIRING PRACTICES
Control, input and motor wiring not separated.
Improper drive grounding.
Improper control wire shielding.
Grounded control signal to grounded drive signal input.
Notes: 101

## Slide 60
UTILITY SUPPLIED VOLTAGE
208/230 VAC OR 460 VAC, +/- 10%
INPUT LINE FUSES OR CIRCUIT BREAKER

## Slide 61
MOVs
> PROTECTS AGAINTS VOLTAGE SPIKES
> CLEARS SPIKE FROM ONE PHASE TO ANOTHER

## Slide 62
ZERO CURRENT TRANSFORMER
> MONITORS INCOMING LINE FOR CURRENT
> LEAKAGE TO GROUND, ACTS LIKE GFCI

## Slide 63
THREE PHASE BRIDGE RECTIFIER
> CONVERTS AC POWER TO DC POWER
> OUTPUTS A PULSATING WAVEFORM

## Slide 64
DC LINE REACTOR
> HELPS TO SMOOTHE CURRENT WAVEFORM

## Slide 65
ELECTROLYTIC CAPACITORS
> CONVERT PULSATING DC INTO CONSTANT DC

## Slide 66
BLEED RESISTORS
> BLEED DOWN VOLTAGE HELD IN CAPACITORS
WHEN LINE VOLTAGE IS REMOVED
> ACT AS VOLTAGE DIVIDER FOR CAPACITORS

## Slide 67
SOFT-START RESISTORS
> SLOWS DOWN CAPACITOR CHARGING CURRENT
WHEN DC BUS IS FIRST ENERGIZED

## Slide 68
SOFT-START RELAY
> REMOVES SOFT-START RESISTORS FROM CIRCUIT
ONCE DC BUS HAS REACHED FULL VOLTAGE

## Slide 69
DC FUSE
> PROTECTS INVERTOR SECTION AGAINST
> USUALLY FAST ACTING FUSE
HIGH CURRENTS

## Slide 70
HALL-EFFECT
> MONITORS LOAD CURRENT AT DC BUS
CURRENT TRANSFORMER

## Slide 71
THREE PHASE INVERTOR
> PROVIDES PWM WAVEFORM TO LOAD
> FAST-FIRING IGBT TECHNOLOGY

## Slide 72
Now if someone,
anyone,
should ask you...
Notes: 38

## Slide 73
Can you
fix this
drive?
Notes: 38

## Slide 74
Your line is...
"YES, I CERTAINLY CAN" !
Notes: 38

## Slide 75
CLASS DISCUSSION