## Slide 1: VFDs
First things first.
Make sure the drive matches the load with at the least these items:
Voltage
Amperage
Horse power
Notes: VFD

## Slide 2: VFDs
Drives can be slightly over sized but never under sized with respect of the load. This is because the amperage range is limited to the HP of the drive.
Drives can operate as many loads as pertains to the job as long as the total horse power, amperage and voltage are not exceeded.
Notes: VFD

## Slide 3: VFDs
A VFD must have a minimum speed setting as anytime the drive contact is closed we put energy on the load.
If we do not have a minimum setting then we cannot cool the motor as the slower the rotor turns the slower the cooling fan turns.
Notes: Look at manufacturers suggestions for minimum settings.

## Slide 4: VFDs
Lets start with some basic programming.
Lets set all drives back to factory defaults.
Notes: VFD

## Slide 5: VFD ABB
Set back to factory default
Go to menu
Go to Assistants
Go to applications
Set to ABB defaults or
Go to HVAC default
Change to another application and save
Switch back to HVAC default
Power down
Power back up
The only thing that should be in the drive is motor information

## Slide 6: VFD Danfoss
Set back to factory default
Press main menu
Select special functions 14-22 (2.1.14( page 21 operation mode
Press ok
Select initialization mode
Power down
Wait 5 minuets then power back up
Back to 14-22 operation mode and select normal operation
Or
Manual with power off. Press status/main menu/ok while powering up

## Slide 7: VFD Yaskawa
Set back to factory default
Go to parameters enter
Go to A1 enter
Set A1-03 page 156 to 2 default value
Power down
Power back up
A1-03 will automatically set back to 0

## Slide 8: VFD Eaton
Set back to factory default
Go to page 240 P21.1.3 619
Switch from 0 to 1 load factory defaults
Power down
Power back up
Switch back to 0

## Slide 9: VFDs
Now lets set time/ date
Down load to the drive/ upload from the drive

## Slide 10: VFD ABB
To set time and date
Go to menu press enter
Go to time and date and change per
To upload download
Go to Menu
Go to parameter backup
Go to menu and press enter
Go to upload and download and change per

## Slide 11: VFD Danfoss
To set time and date
Go to main menu OK
Go to references ramps ok
Go to parameter 3.2.8 0-7 page 33 and follow the prompts
To upload download
Go to main menu OK
Go to parameter 3.2.6 0-2 page 32 and follow prompts

## Slide 12: VFD Yaskawa
To set time and date
Go to programming
Go to parameter o4-17 page 191
Set to 1 HOA keypad to adjust time and date
To set upload download
Go to parameter o3-09 page 189 and follow the prompts

## Slide 13: VFD Eaton
Set time and date on Eaton drives
Go to p21.4.1 page 68 and set time/date
Set upload download
Go to parameter p21.1.4 620 and follow prompts

## Slide 14: VFD ABB
Setting applications
Go to menu enter
Go to Assistants enter
Go to applications enter
Select application save
HVAC default, Supply fan, return fan, ect.

## Slide 15: VFD Danfoss
Setting applications
Go to quick menu page 16 ok
Go to function set up ok
Go to set applications ok
Select application ok

## Slide 16: VFD Yaskawa
Set applications
Go to A1-06 page 124
Scroll down select application enter
Set to specified number enter

## Slide 17: VFD Eaton
Set applications
Go to P1.13 page 56
Scroll down and find your application and enter

## Slide 18: VFD ABB
Set up internal PID loop/closed loop application
Go to page 274 explanation of PID loop
Go to page 277 parameter 4001 through page 289 parameter 4020
Follow prompts
Or go to menu
Go to assistants
Go to PID loop control

## Slide 19: VFD Danfoss
Set up internal/closed loop application
Go to quick menus enter OK
Go to function setups enter OK
Go to closed loop applications enter OK
Follow prompts

## Slide 20: VFD Yaskawa
Set up internal/closed loop application
Go to page 323 S3-01-324 S3-17
Follow prompts

## Slide 21: VFD Eaton
Set up internal/closed loop application
Go to M-34 page 86
Follow prompts

## Slide 22: VFD ABB
Changing keypad information
Go to parameters 3400
Change line one save and change back save
Change line two save and change back save
Change line three save and change back save

## Slide 23: VFD Danfoss
Changing keypad information
Go to main menu enter
Go to O operation display OK
Go to LCP display
Make changes to 1.1, 1.2, 1.3, 2, 3 save
Change back then save or go back to default

## Slide 24: VFD Yaskawa
Changing keypad information
Go to parameters enter
Go to O enter
Select monitor line to change enter

## Slide 25: VFD Eaton
Changing keypad
Go to M-monitor enter
Select what you want to change enter

## Slide 26: VFD ABB
Auto tuning
Go to parameter 2305 enter
Change to on save
Put drive in hand at 20 htz
Let drive take over
Drive automatically saves back to off

## Slide 27: VFD Danfoss
Auto tune (AMA)
Go to main menu
Go to load and motor OK
Go to 1.2 motor data OK
Go to 1-29 OK
Set AMA or reduced AMA
Set drive to hand
Drive will reset when done

## Slide 28: VFD Yaskawa
Auto tune motor
Go to T1-01 enter
Set to 2 enter
When done set to 3 enter
When done drive will return to normal

## Slide 29: VFD Eaton
Auto tune

## Slide 30: VFD ABB
Set minimum/maximum Frequency
Go to menu enter
Go to parameters enter
Go to limits 2000 enter
Go to Minimum setting 2007 enter
Set minimum save
Go to maximum setting 2008 enter
Set maximum setting

## Slide 31: VFD Danfoss
Set minimum/maximum Frequency
Go to main menu OK
Go to 4 limits/warnings OK
Go to 4-1 motor limits OK
Go to 4-12 motor speed low limit OK
Enter minimum speed OK
Go to 4-14 motor speed high limit OK
Enter maximum speed

## Slide 32: VFD Yaskawa
Set minimum speed
Go to programming enter
Go to d2-02 enter
Set minimum
Go to d2-01 enter
Set maximum setting

## Slide 33: VFD Eaton
Set minimum/maximum Frequency
Go to P parameters enter
Go to P1 basic parameters enter
Go to P1.1 minimum frequency enter
Set minimum enter
Go to P1.2 maximum frequency enter
Set maximum frequency

## Slide 34: VFD ABB
Set accel/decel
Go to menu enter
Go to parameters enter
Go to parameter 2200 Accell/Decell enter
Go to 2202/2203 enter
Set speeds

## Slide 35: VFD Danfoss
Set accel/decel
Go to main menu OK
Go to reference/ramps 3 OK
Go to ramp up 3-42 set
Go to ramp down 3-42 set

## Slide 36: VFD Yaskawa
Set accel/decel
Go to programming enter
Go to c1-01 enter set accel
Go to c1-02 enter set decel

## Slide 37: VFD Eaton
Set accel/decel
Go to menu OK
Go to P.1 OK
Go to P.1.3 OK set accel
Go to P1.4 OK set decel