## Slide 1: Why Use a VFD? “How do VFDs Save Money?”
ABB Low Voltage Drives, USA

## Slide 2: HVAC Applications for Variable Frequency Drives
Why use a VFD?
  Flexible electronic speed control
  Simple to install
  Improves Performance
  Low maintenance
    VFD
    Driven equipment
  Improved Equipment Life
    Reduced wear and tear
    Reduced peak starting currents
  High Efficiency >>> Saves Energy$$
Why use a VFD?
Slide 2
Notes: ACH550 is a very capable and adaptable drive
Drives in general can be easily inserted into existing systems Drive replaces the starter in most cases
Operational performance and Energy performance are improved
Easy to maintain and they can extend system life cycle times by reducing Wear and Tear
Not only are you saving Energy…
you are helping to improve the equipment’s operating life and the overall life cycle of the system through Reduced wear and tear.

## Slide 3: HVAC Applications for Variable Frequency Drives
“When you can Optimize the energy delivered into a System by controlling Flow or Pressure”
HVAC systems are designed for worst-case situations…
  the coldest days in winter
  the hottest, most humid days in summer with the highest occupancy
At all other times, the HVAC system is Oversized
By Optimizing (Reducing) system capacity…
  energy is saved
  occupant comfort is improved
When to use a VFD?
Slide 3
Notes: When? To use a VFD?
When you can affect how much Energy is needed to meet the performance needs of the system
Emphasize the Oversized

## Slide 4: HVAC Applications:
Chart: Flow (GPM)
| 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Pump Curve | 50 | 49.9556 | 49.8222 | 49.6 | 49.2889 | 48.8889 | 48.4 | 47.8222 | 47.1556 | 46.4 | 45.5556 | 44.6222 | 43.6 | 42.4889 | 41.2889 | 40 | 38.6222 | 37.1556 | 35.6 | 33.9556 | 32.2222
Control Curve | 5 | 5.1556 | 5.6222 | 6.4 | 7.4889 | 8.8889 | 10.6 | 12.6222 | 14.9556 | 17.6 | 20.5556 | 23.8222 | 27.4 | 31.2889 | 35.4889 | 40 | 44.8222 | 49.9556
Chart: Flow (GPM)
| 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Pump Curve | 50 | 49.9556 | 49.8222 | 49.6 | 49.2889 | 48.8889 | 48.4 | 47.8222 | 47.1556 | 46.4 | 45.5556 | 44.6222 | 43.6 | 42.4889 | 41.2889 | 40 | 38.6222 | 37.1556 | 35.6 | 33.9556 | 32.2222
Control Curve | 5 | 5.1556 | 5.6222 | 6.4 | 7.4889 | 8.8889 | 10.6 | 12.6222 | 14.9556 | 17.6 | 20.5556 | 23.8222 | 27.4 | 31.2889 | 35.4889 | 40 | 44.8222 | 49.9556
Optimize capacity to meet changing system demands in… Flow and Pressure
How do VFDs save energy?
Slide 4
Pump Curve
Control Curve
Operating Point
Notes: To explore “How” the VFDs save Energy let’s take a moment to review the typical Pump Control scenario
Energy applied to a Motor + Pump generates the Pressure needed to create the Flow in the system.

## Slide 5: HVAC Applications:
Chart: Flow (GPM)
| 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Pump Curve | 50 | 49.9556 | 49.8222 | 49.6 | 49.2889 | 48.8889 | 48.4 | 47.8222 | 47.1556 | 46.4 | 45.5556 | 44.6222 | 43.6 | 42.4889 | 41.2889 | 40 | 38.6222 | 37.1556 | 35.6 | 33.9556 | 32.2222
Control Curve | 5 | 5.1556 | 5.6222 | 6.4 | 7.4889 | 8.8889 | 10.6 | 12.6222 | 14.9556 | 17.6 | 20.5556 | 23.8222 | 27.4 | 31.2889 | 35.4889 | 40 | 44.8222 | 49.9556
First… Let’s understand the Power required to achieve the operating condition
How do VFDs save energy?
Slide 5
Flow
Pressure
Power α Pressure x Flow
Operating Point

## Slide 6: HVAC Applications:
Changing the Flow in the system by changing the pressure acting in the system
  Traditional Method:
    Adding a Flow restriction
    Increased Pressure
    Reduced flow
    Little reduction in pump energy
  Efficient Method:
    VFD to reduce Motor/Pump speed
    Reduced pressure
    Reduced flow
    Reduced pump energy
Classic Retro-fit Opportunity! $$$
How do VFDs save energy?
Slide 6
Retro-Fit!
Notes: A classic Retro-fit opportunity is replacing a mechanically restricted control of a water system with a VFD controlling the pump speed to change and manage the flow in the system.
Systems with Bypasses that recirculate the Air or Water to reduced Supply volumes instead of reducing the flow by slowing down the speed of the motor turning the Fan or Pump.
Changes to the system need to be made to the system to change the Flow in the system.

## Slide 7: HVAC Applications:
Chart: Flow (GPM)
| 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Pump Curve | 50 | 49.9556 | 49.8222 | 49.6 | 49.2889 | 48.8889 | 48.4 | 47.8222 | 47.1556 | 46.4 | 45.5556 | 44.6222 | 43.6 | 42.4889 | 41.2889 | 40 | 38.6222 | 37.1556 | 35.6 | 33.9556 | 32.2222
Control Curve | 5 | 5.1556 | 5.6222 | 6.4 | 7.4889 | 8.8889 | 10.6 | 12.6222 | 14.9556 | 17.6 | 20.5556 | 23.8222 | 27.4 | 31.2889 | 35.4889 | 40 | 44.8222 | 49.9556
Traditional Method: Adding a Flow Restriction (Valve, Inlet Guide vanes, etc.) to change the Flow.
How do VFDs save energy?
Slide 7
Wasted Energy
Notes: Instead of 1500 GPM of flow… the system requires 1000 GPM of flow.
Traditional method first…
Restricting the flow by “pinching down” the control valve the Operating point rides the pump curve to achieve the new flow at a higher pressure.
If the Area is the Energy Which flow point requires more energy?
Which Area is smaller Yellow or Orange?
In some case it may Require more pump Energy to provide less flow.

## Slide 8: HVAC Variable Torque Applications for VFDs
Efficient Method: Using a VFD to reduce pump speed and power to manage the pressure needed >>> required flow
How do VFDs save energy?
Slide 8
Notes: The required flow as an Input to the Control system (measured as Differential Pressure)
changes in the system to create the needed pressure… to achieve the desired Operating Point.
Need enough pressure to create the design flow through that last coil set.
Sensor placement is key. The better “tap” location for the Supply and Return line pressures pick-up is typically out on the main Supply and return lines just before and after the branch line take-offs.
Watch out for taps located right at the coils set or in the branch lines to the coils. The motion of the valve (or lack of motion i.e. Closed ) can be an unreliable indication of differential pressure.

## Slide 9: HVAC Variable Torque Applications for VFDs
Chart: Flow (GPM)
| 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Pump Curve | 50 | 49.9556 | 49.8222 | 49.6 | 49.2889 | 48.8889 | 48.4 | 47.8222 | 47.1556 | 46.4 | 45.5556 | 44.6222 | 43.6 | 42.4889 | 41.2889 | 40 | 38.6222 | 37.1556 | 35.6 | 33.9556 | 32.2222
Control Curve | 5 | 5.1556 | 5.6222 | 6.4 | 7.4889 | 8.8889 | 10.6 | 12.6222 | 14.9556 | 17.6 | 20.5556 | 23.8222 | 27.4 | 31.2889 | 35.4889 | 40 | 44.8222 | 49.9556
Chart: Flow (GPM)
| 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000
Pump Curve | 50 | 49.9556 | 49.8222 | 49.6 | 49.2889 | 48.8889 | 48.4 | 47.8222 | 47.1556 | 46.4 | 45.5556 | 44.6222 | 43.6 | 42.4889 | 41.2889 | 40 | 38.6222 | 37.1556 | 35.6 | 33.9556 | 32.2222
Control Curve | 5 | 5.1556 | 5.6222 | 6.4 | 7.4889 | 8.8889 | 10.6 | 12.6222 | 14.9556 | 17.6 | 20.5556 | 23.8222 | 27.4 | 31.2889 | 35.4889 | 40 | 44.8222 | 49.9556
Reduced Flow Pump Curve | 26 | 25.94 | 25.76 | 25.46 | 25.04 | 24.5 | 23.84 | 23.06 | 22.16 | 21.14 | 20 | 18.74 | 17.36 | 15.86 | 14.24
The VFD+system can follow the Control Curve to generate the reduced pressure needed to achieve the appropriate flow.
How do VFDs save energy?
Slide 9
Energy
Saved
Notes: New pump curve at reduced speed (<60Hz)… generates required Pressure and Flow at significantly lower Energy $$.
Which Area is smaller Green or Yellow?
Reducing the Flow by 1/3rd reduces the power by 70%.
Or
30% of the Power to deliver the 2/3rds of the Flow