## Slide 1: Energy Efficiency - Fans VFD or Not?
HVAC Sales School

## Slide 2: VFD or Not? Scenario 1 Energy Efficiency
No Flow Control on Supply Fan (365 days/year)
Monday through Friday
  6:00 AM to 6:00 PM the flow required averages 50%.
  6:00 PM to 6:00 AM the flow required averages 0%.
  Saturday & Sunday
    The flow required averages 0%.

## Slide 3: VFD or Not? Scenario 2 Energy Efficiency
No Flow Control on Supply Fan (365 days/year)
Monday through Friday
  6:00 AM to 6:00 PM the flow required averages 90%.
  6:00 PM to 6:00 AM the flow required averages 0%.
Saturday & Sunday
  The flow required averages 0%.

## Slide 4: VFD or Not? Scenario 3 Energy Efficiency
Inlet Vane Control (365 days/year) on Air Handler
Monday through Friday
  7:10 AM to 4:45 PM the flow required averages 70%
  4:45 PM to 7:10 PM the flow required averages 50%
  7:10 PM to Midnight the flow required averages 40%
  Midnight to 7:10 AM the flow required averages 20%
Saturday & Sunday
  The flow required is 0%

## Slide 5: VFD or Not? Scenario 4 Energy Efficiency
Outlet Damper Control (365 days/year) on Air Handler
Monday through Friday
  70% Flow 40%
  50% Flow 10%
  40% Flow 20%
  20% Flow 30%
  Saturday & Sunday
  The fan is off

## Slide 6: VFD or Not? Scenario 5 Energy Efficiency
Inlet Vane Control (365 days/year) on Air Handler
Monday through Friday
  Throughout an average day the flow required is: Full Flow 5% 90% Flow 10% 80% Flow 15% 70% Flow 20% 60% Flow 20% 50% Flow 15% 40% Flow 10% 30% Flow 5%
Saturday & Sunday
  The fan is off

## Slide 7: VFD or Not? Scenario 6 Energy Efficiency
Outlet Damper Control (365 days/year) on Air Handler
Monday through Friday
  Throughout an average day the flow required is: Full Flow 5% 90% Flow 10% 80% Flow 15% 70% Flow 20% 60% Flow 20% 50% Flow 15% 40% Flow 10% 30% Flow 5%
Saturday & Sunday
  The fan is off

## Slide 8: VFD or Not? Energy Efficiency
Improved Flow Control by
  ABB Drive series: ACH550
CO2 emission/unit 0.5
Economic Data
  Currency $
  Energy Price (per kWh) 0.1
  Investment Cost 5.7K
  Interest Rate (%) 4
  Service Life (years) 10
Fan Data
  Fan Type Centrifugal
  Impeller Type Backward Curved
  Nominal Volume Flow 75000
  Pressure Increase 2.5
  Efficiency 78
Transmission
  Efficiency 100
Motor & Supply Data
  Supply Voltage 460
  Motor Power 50
  Motor Efficiency 95