## Slide 1: Energy Efficiency - Pumps VFD or Not?
HVAC Sales School

## Slide 2: VFD or Not? Scenario 1 Energy Efficiency
On/Off Control (365 days/year)
Monday through Friday
  6:00 AM to 6:00 PM the pump cycles 10 minutes on and 10 minutes off.
  6:00 PM to 6:00 AM the pump is off.
Saturday & Sunday
  The pump is off

## Slide 3: VFD or Not? Scenario 2 Energy Efficiency
On/Off Control (365 days/year)
Monday through Friday
  6:00 AM to 6:00 PM the pump cycles 90 minutes on and 10 minutes off.
  6:00 PM to 6:00 AM the pump is off.
Saturday & Sunday
  The pump is off

## Slide 4: VFD or Not? Scenario 3 Energy Efficiency
On/Off Control (365 days/year)
Monday through Friday
  7:10 AM to 4:45 PM the pump cycles 14 minutes on and 6 minutes off.
  4:45 PM to 7:10 PM the pump cycles 10 minutes on and 10 minutes off.
  7:10 PM to Midnight the pump cycles 8 minutes on and 12 minutes off.
  Midnight to 7:10 AM the pump cycles 4 minutes on and 16 minutes off.
Saturday & Sunday
  The pump is off

## Slide 5: VFD or Not? Scenario 4 Energy Efficiency
Throttling Control (365 days/year)
Monday through Friday
  7:10 AM to 4:45 PM the demand averages 70%
  4:45 PM to 7:10 PM the demand averages 50%
  7:10 PM to Midnight the demand averages 40%
  Midnight to 7:10 AM the demand averages 20%
Saturday & Sunday
  The pump is off

## Slide 6: VFD or Not? Scenario 5 Energy Efficiency
On/Off Control (365 days/year)
Two identical pumps of equal capacity
Monday through Friday
  6:00 AM to 6:00 PM pump one runs continuously and pump two cycles 40 minutes on and 10 minutes off.
  6:00 PM to 6:00 AM pump one runs continuously. Pump two is off.
Saturday & Sunday
  6:00 AM to 6:00 AM pump one cycles 40 minutes on and 10 minutes off. Pump two is off.

## Slide 7: VFD or Not? Scenario 6 Energy Efficiency
Throttling Control
Monday through Friday
  Throughout an average day the demand varies between 30% and 100% flow Full Flow 5% 90% Flow 10% 80% Flow 15% 70% Flow 20% 60% Flow 20% 50% Flow 15% 40% Flow 10% 30% Flow 5%
Saturday & Sunday
  The pump is off

## Slide 8: VFD or Not? Energy Efficiency
System Data
  Liquid Density 62
  Static head 20
Pump Data
  Nominal Flow Volume 3000
  Nominal head 60
  Maximum head 70
  Efficiency 75
Motor & Supply Data
  Motor Power 75
  Supply Voltage 460
  Motor Efficiency 95
Improved Flow Control by
  ABB Drive series: ACH550
CO2 emission/unit 0.5
Economic Data
  Currency $
  Energy Price (per kWh) 0.1
  Investment Cost 7.4K
  Interest Rate (%) 4
  Service Life (years) 10

## Slide 9: VFD or Not? Energy Efficiency
System Data
  Liquid Density 62
  Static head 20
Pump Data
  Nominal Flow Volume 6000
  Nominal head 60
  Maximum head 70
  Efficiency 75
Motor & Supply Data
  Motor Power 150
  Supply Voltage 460
  Motor Efficiency 95
Improved Flow Control by
  ABB Drive series: ACH550
CO2 emission/unit 0.5
Economic Data
  Currency $
  Energy Price (per kWh) 0.1
  Investment Cost
  Single Drive 12.5K
  Dual Drive 14.8K
  Interest Rate (%) 4
  Service Life (years) 10