## YK
Chiller Preventive Maintenance Kits
Preventive Maintenance Kits for the most popular chiller models provide what you need for annual servicing in one easy-to-order package. For each chiller maintenance, you’ll need:
1. Preventive Maintenance Parts Kit
2. York® oil
3. Inhibitor (coolant)
You’ll find the order numbers below, by chiller series and style.
You will also need evaporator and condenser head gasket material. It comes in two types, channel or bulb type, and both types comes in 25-foot and 50-foot rolls. Each machine needs a different length. Verify the length need in the unit's parts book or provide the unit's model and serial number to the customer service representative when you call.
| Part # | Description |  | What you need to know to order
| 028 03242 025 | 25' bulb type |  | How many passes in the evaporator or condenser?
| 028 03232 050 | 50' bulb type |  | Is vessel 150 psi or 300 psi rated? (Find on unit data plate)
| 028 09951 025 | 25'channel type |  | Standard or marine water boxes?
| 028 09951 050 | 50' channel type (U shaped)
Chiller Type-Evap.Code,Cond.Code,Comp.Size-Motor Code,Style(11th digit)
Model # YTA1A3C1-CKE
Preventive Maintenance Kit |  | YK Series Style A, B, C
Parts Kit | Chiller Type | Part # | Quantity | Description | What to order
| YK Series Style A, B, C | 366 94952 013 | 2 | Oil return filter drier | Order one kit per chiller
|  |  | 1 | Strainer 1/4" male
|  |  | 1 | Oil filter (10" long, 5 micron) with internal spring
|  |  | 1 | Oil filter gasket kit
Oil | YK Series Style A, B C with size G, H & J compressor using R-22 refrigerant | 011 00434 000 (5 gal container) | 4 containers | 20 gals York F oil | Order number of containers shown. Always buy only genuine York oil.
| YK Series Style A, B, C with size G, H & J compressor using R-134A refrigerant | 011 00533 000 (5 gal container) | 4 containers | 20 gals York K Oil
Coolant | YK Series Style A, B, C with solid state starter | 013 02987 000 (1 gal container) | 1 container | Inhibitor (coolant) | Order number of containers shown. Inhibitor must be changed annually or sooner if it has become cloudy or brown in color. Never reuse coolant!
| YK Series Style A, B, C with VSD | 013 02987 000 (1 gal container) | 3 containers | Inhibitor (coolant)
Preventive Maintenance Kit |  | YK Series Style D & E
Choose one of the two parts kits based on the chiller's oil filter housing
| Chiller Type | Part # | Quantity | Description | What to order
Parts Kit 1 | YK Series Style D & E (long filter without threaded collar) | 366 94952 014 | 1 | Oil return filter drier | Order one kit per chiller
|  |  | 1 | Oil filter gasket kit
|  | 392 10719 000 | 1 | Oil filter (10" long, 5 micron) w/internal spring | Order separately -- not included in kit
Parts Kit 2 | YK Series Style D & E (short filter with threaded collar) | 366 94952 015 | 1 | Oil return filter drier | Order one kit per chiller
|  |  | 1 | Oil filter (3 micron)
|  | 028 14404 000 | 1 | O-ring | Order separately -- not included in kit
Oil | YK Series Style D & E with size G,H & J compressor using R-134A refrigerant | 011 00533 000 (5 gal container) | 4 containers | 20 gals York K Oil | Order number of containers shown. Always buy only genuine York oil.
Coolant | YK Series Style D & E with solid state starter | 013 02987 000 (1 gal container) | 1 container | Inhibitor (coolant) | Order number of containers shown. Inhibitor must be changed annually or sooner if it has become cloudy or brown in color. Never reuse coolant!
| YK Series Style D & E with VSD | 013 02987 000 (1 gal container) | 3 containers | Inhibitor (coolant)
Preventive Maintenance Kit |  | YK Series Style F &G
| Chiller Type | Part # | Quantity | Description | What to order
Parts Kit | YK Series Style F & G | 366 94952 016 | 1 | Oil filter (3 micron) | Order one kit per chiller
|  |  | 1 | O-ring
|  |  | 1 | Drier C-30E85, Sporlan #
|  |  | 2 | Drier seal rings
|  | 028 15798 000 | 1 | Style G oil filter gasket | Order separately -- not included in kit
Oil | YK Series Style F with G, H, J, P6-P9 compressor using R-134A refrigerant | 011 00533 000 (5 gal container) | 4 containers | 20 gals York K oil (10 gals for P1-P5, Q7 compressor on Style F) | Order number of containers shown. Always buy only genuine York oil.
Coolant | YK Series Style F&G with solid state starter | 013 02987 000 (1 gal container) | 1 container | Inhibitor (coolant) | Order number of containers shown. Inhibitor must be changed annually or sooner if it has become cloudy or brown in color. Never reuse coolant!
| YK Series Style F&G with VSD | 013 02987 000 (1 gal container) | 3 containers | Inhibitor (coolant)

## YS
Preventive Maintenance Kit |  | YS Series Style C
| Chiller Type | Part # | Quantity | Description | What to order
Parts Kit | YS Series Style C | 366 94952 017 | 2 | 8” x 3”element for dual or single filters, numbers on oil filter housing | Order one kit per chiller.
|  |  | 1 | O-ring kit for 026-32831 (2 O-rings in kit)
|  |  | 2 | Rotolock suction filter
|  |  | 1 | Rotolock filter drier
|  |  | 6 | Seal rings (2 per filter) |  | Two per filter would be 4, not 6
Oil | YK Series Style C with size SO compressor using R22 refrigerant | 011 00312 000 (5 gal container) | 2 containers | 10 gals York C oil | Order number of containers shown. Always buy only genuine York oil.
| YK Series Style C with size SO compressor using R134A refrigerant | 011 00549 000 (5 gal container) | 2 containers | 10 gals York H oil
Coolant | YK Series Style C with solid state starter | 013 02987 000 (1 gal container) | 1 container | Inhibitor (coolant) | Order number of containers shown. Inhibitor must be changed annually or sooner if it has become cloudy or brown in color. Never reuse coolant!
| YK Series Style C with VSD | 013 02987 000 (1 gal container) | 3 containers | Inhibitor (coolant)
Preventive Maintenance Kit |  | YS Series Style D & E
| Chiller Type | Part # | Quantity | Description | What to order
Parts Kit | YS Series Style D & E | 366 94952 018 | 1 | 8” x 3” element for dual filters | Order one kit per chiller.
|  |  | 1 | O-ring kit for 026-32831 (single filters)
|  |  | 2 | Rotolock suction filter
|  |  | 1 | Rotolock filter drier
|  |  | 6 | Seal rings (2 per filter) |  | Two per filter would be 4, not 6
Oil | YK Series Style D & E with size SO compressor using R22 refrigerant | 011 00312 000 (5 gal container) | 2 containers | 10 gals York C oil | Order number of containers shown. Always buy only genuine York oil.
| YK Series Style D & E with size SO compressor using R134A refrigerant | 011 00549 000 (5 gal container) | 2 containers | 10 gals York H oil
Coolant | YK Series Style D & E with solid state starter | 013 02987 000 (1 gal container) | 1 gal | Inhibitor (coolant) | Order number of containers shown. Inhibitor must be changed annually or sooner if it has become cloudy or brown in color. Never reuse coolant!
| YK Series Style D & E with VSD | 013 02987 000 (1 gal container) | 3 containers | Inhibitor (coolant)

## YT
Preventive Maintenance Kit |  | YT Series Style A – G
| Chiller Type | Part # | Quantity | Description | What to order
Parts Kit | YT Series Style A through G | 366 94952 009 | 1 | Oil return filter ½” flare, 30 cu in | Order one kit per chiller
|  |  | 1 | Purge filter ½” flare, 30 cu in
|  |  | 1 | Purge strainer ¼”
|  |  | 1 | Purge strainer 3/8” (used on pump-assisted purges)
|  |  | 1 | Oil filter (10 long, 5 micron) w/internal spring
|  |  | 1 | Gasket kit
Oil | YT Series Style A & B-using R11 and R123 refrigerant | 011 00312 000 (5 gal container) | 3 containers | 13 gals York C oil | Order number of containers shown. Always buy only genuine York oil. | 13?
| YT Series Style C & D with size B and C compressors using R11 and R123 refrigerant |  | 2 containers | 10 gals York C oil
| YT Series Style C & D with size E compressor using R11 and R123 refrigerant |  | 3 containers | 15 gals York C oil
| YT Series Style C & D with size F compressor using R11 and R123 refrigerant |  | 4 containers | 20 gals York C oil
| YT Series Style E, F & G with size B and C compressors using R11 and R123 refrigerant |  | 2 containers | 10 gals York C oil
| YT Series Style E, F & G with size E and F compressors using R11 and R123 refrigerant |  | 3 containers | 15 gals York C oil
Coolant | YT Series Style C, D & E with solid state starter | 013 02987 000 (1 gal container) | 1 container | Inhibitor (coolant) | Order number of containers shown. Inhibitor must be changed annually or sooner if it has become cloudy or brown in color. Never reuse coolant!
| YT Series Style C, D & E with VSD | 013 02987 000 (1 gal container) | 3 containers | Inhibitor (coolant)
What about YT A, B, E, F&G coolant?
Preventive Maintenance Kit |  | YT Series Style H
| Chiller Type | Part # | Quantity | Description | What to order
PM Kit | YT Series Style H | 366 94952 010 | 1 | Oil filter (9.75 long , 10 micron) | Order 1 kit per chiller
|  |  | 1 | Gasket kit
|  |  | 1 | Oil return filter ½” flare, 30 cu in
|  |  | 1 | Purge filter ½” flare, 30 cu in
|  |  | 1 | Purge strainer ¼”
|  |  | 1 | Purge strainer 3/8” (used on pump-assisted purges)
Oil | YT Series Style H size with B and C compressors using R11 and R123 refrigerant | 011 00312 000 (5-gallon container) | 2 containers | 10 gals York C oil | Order number of containers shown. Always buy only genuine York oil.
| YT Series Style H with size E and F compressors using R11 and R123 refrigerant |  | 3 containers | 15 gals York C oil
Coolant | YK Series Style H with solid state starter | 013 02987 000 (1 gal container) | 1 container | Inhibitor (coolant) | Order number of containers shown. Inhibitor must be changed annually or sooner if it has become cloudy or brown in color. Never reuse coolant!
| YK Series Style H with VSD | 013 02987 000 (1 gal container) | 3 containers | Inhibitor (coolant)
| Preventive Maintenance Kit | YT Series Style J
Choose one of the two parts kits based on the chiller's oil filter housing
| Chiller Type | Part # | Quantity | Description | What to order
Parts Kit 1 | YT Series Style J (long filter without threaded collar) | 366 94952 011 | 1 | Oil filter (10 micron) | Order one kit per chiller.
|  |  | 1 | Gasket kit
|  |  | 1 | Purge filter ½” flare, 30 cu in
|  |  | 2 | Seal ring for 026-32841-000
|  |  | 1 | Oil return drier (Rotolock)
|  |  | 1 | Purge strainer 3/8” (used on pump-assisted purges)
Parts Kit 2 | YT Series Style J (short filter with threaded collar) | 366 94952 012 | 1 | Oil filter (8.19 long, 10 micron) | Order one kit per chiller.
|  |  | 1 | O-ring
|  |  | 1 | Purge filter ½” flare, 30 cu in
|  |  | 2 | Seal ring for 026-32841-000
|  |  | 1 | Oil return drier (Rotolock)
Oil | YT Series Style J with size B and C compressors using R11 and R123 refrigerant | 011 00312 000 (5-gallon container) | 2 containers | 10 gals York C oil | Order number of containers shown. Always buy only genuine York oil.
| YT Series Style J with size E and F compressors using R11 and R123 refrigerant |  | 3 containers | 15 gals York C oil
Coolant | YT Series J with solid state starter | 013 02987 000 (1 gal container) | 1 container | Inhibitor (coolant) | Order number of containers shown. Inhibitor must be changed annually or sooner if it has become cloudy or brown in color. Never reuse coolant!
| YT Series J with VSD | 013 02987 000 (1 gal container) | 3 containers | Inhibitor (coolant)