This standard, defining the requirements of materials to be furnished or

services to be performed, is not subject to interpretation.

1.	SCOPE

  - This standard covers molded elastomer seals, O-rings, made for

commercial refrigeration application.

2.	RELATED STANDARDS

2.1	The molded elastomer seals supplied under this standard shall be tested to the following appropriate ASTM Specification, or by the YORK Test Method as indicated.

- ASTM D 395, Latest Rev.: Rubber Property - Compression Set

- ASTM D 412, Latest Rev.: Vulcanized Rubber and Thermoplastic Rubbers and Thermoplastic Elastomers Tension

- ASTM D 471, Latest Rev.: Rubber Property - Effect of Liquids

- ASTM D 573, Latest Rev.: Rubber Deterioration In An Air Oven

- ASTM D 2240, Latest Rev.: Rubber Property - Durometer Hardness

- York R-1142: General Requirements for O-Ring Grooves and O-Ring Application.

- SAE ARP 5316 Rev. B.: Storage of Elastomer Seals and Seal Assemblies.

- Military Standard MIL-STD-413, Latest Rev.: Visual Inspection Guide for O-rings.

- Aerospace Standard AS-568A Rev. 1974: Size Standard for O-rings.

- Rubber Manufacturers Association sStandard RMA MO-1 Rev 1992: 
Rubber Handbook

3.	MATERIAL CHARACTERISTICS

  - The mechanical and physical properties of the seal materials shall be as shown in Table 3.1(a) through 3.1(e).

3.1	(Continued)

- Properties As Molded (At room Temperature).

TABLE 3.1(a)

|  | ASTM |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| CHARACTERISTICS | TEST | NEOPRENE | NEOPRENE-1 | BUNA N | Viton, Fluorel | HNBR |
|  | SPEC |  |  |  |  |  |
| Hardness, Shore A Durometer | D 2240 | 60-75 | 65-75 | 60-70 | 70-80 | 60-75 |
| Tensile Strength, psi min. | D 412 | 1500 | 1015 | 1500 | 1400 | 2000 |
| Ultimate Elongation, % min. | D 412 | 225 | 150 | 250 | 125 | 250 |
| Compression Set, % max. | D 395 Method B | 25* | 30 | 25* | Under .11” 20% Over .11” 15% | 25* |
| Specific Gravity | -------- | *** | *** | *** | *** | *** |
| * - Percentage of original deflection after 22 hours at 212F. ** - Percentage of original deflection after 70 hours at 75 5F max. *** - As determined for specific compound. |  |  |  |  |  |  |

(b)  Properties After Heat Aging shall be as shown in Table 3.1(b)

TABLE 3.1(b)

|  | ASTM .0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| CHARACTERISTICS | TEST . | NEOPRENE | NEOPRENE-1 | BUNA N | Viton, Fluorel | HNBR . |
|  | SPEC. . |  |  |  |  |  |
| Hardness, points change max. | D 573 . | +10 . | +10 . | +10 . | +10 / -5 | +10 . |
| Tensile Strength, % change max. | D 573 . | -10 . | -10 . | -10 . | -35 | -10 . |
| Elongation, % change max. | D 573 . | -45 . | -45 . | -45 . | -15 | -10 . |
| (1) 70 hours at 212F for Neoprene and Buna N. |  |  |  |  |  |  |
| (2) 70 hours at 528F for Viton and Fluorel. |  |  |  |  |  |  |

(c)  Properties After Oil Aging shall be as shown in Table 3.1(c).

TABLE 3.1(c)

|  | ASTM |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Characteristics | Test | Neoprene | Neoprene-1 | Buna N | Viton, Fluorel | HNBR |  |
|  | Spec. |  |  |  |  |  |  |
| Hardness, points change max. | D 471 | -15 | -15 | -10 | 0-15 | -10 |  |
| Volume, % change max. | D 471 | +33 | +33 | +5 | 0-20 | +20 |  |
| Tensile Strength, % change max. | D 471 | --- | --- | --- | 30 | -10 |  |
| Elongation, % change max. | D 471 | --- | --- | --- | -20 | -10 |  |
| (1) 70 hours at 212F in YORK “C” Oil; Neoprene and Buna N. |  |  |  |  |  |  |
| (2) 70 hours at 347 5F in Stauffer Blend 7700; Viton and Fluorel. |  |  |  |  |  |  |

(d)  Resistance To Liquid Refrigerants With Oil shall be as shown

in Table 3.1(d).

TABLE 3.1(d)

| Characteristics | Neoprene | Neoprene-1 | Buna N | Viton, Fluorel | HNBR |
| --- | --- | --- | --- | --- | --- |
| R-11 Thickness Increase, % max. | 20 | 20 | 20 | 10 | NA |
| R-12 Thickness Increase, % max. | 5 | NA | 5 | 8 | NA |
| R-22 Thickness Increase, % max. | 6 | 8 | NR | NR | 36 |
| R-123 Thickness Increase, % max. | NR | 15 | NR | NR | NR |
| R-134a Thickness Increase, % max. | 7 | 7 | NA | NA | 20 |
| R-11 Hardness points change, max. | -15 | -10 | -15 | -20 | NA |
| R-12 Hardness points change, max. | -10 | NA | -10 | -20 | NA |
| R-22 Hardness points change, max. | -15 | -5 | NR | NR | -12 |
| R-123 Hardness points change, max. | NR | -10 | NR | NR | NR |
| R-236fa Hardness points Change, max. | -8~ +5 | -8~ +5 | NA | NA | -6 |
| NA = NO DATA AVAILABLE |  |  |  |  |  |
| NR = NOT RECOMMENDED |  |  |  |  |  |
| (1) 93% refrigerant, 7% YORK “C” oil by weight. |  |  |  |  |  |
| (2) One (1) week immersion at room temperature. |  |  |  |  |  |

- Chemical Stability shall be as shown in Table 3.1(e).

The chemical stability test is an evaluation of the elastomer materials that simulates the hardening, flattening, cracking and loss of strength which occurs with exposure to refrigerant, and shall be performed as described in ASTM D471.

NOTE: Appropriate steps are to be taken to insure the test equipment is suitable to contain the refrigerant pressures at the specified test conditions.

TABLE 3.1(e)

| Characteristics |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Neoprene | Neoprene-1 | Buna N | Viton, Fluorel | HNBR |
| Tensile Strength, Decrease max. |  | 55 | 55 | 55 | 65 | 55 |
| Elongation, % change max. |  | -50 | -50 | -50 | -25 | -50 |
| Shore Hardness | Points increase | 0 | 0 | 0 | 0 | 0 |
|  | Points decrease | 10 | 10 | 10 | 20 | 10 |
| (1) 21 days exposure (R-134a and air) at 200F. |  |  |  |  |  |  |

4.	DIMENSIONAL TOLERANCES

4.1	O-Rings shall be molded to the dimensions and shape (cross-section) as specified with tolerances per AS 568A Rev 1974.

4.2	O-Rings shall be free of surface defects, indentations and cuts. NOTE:  MIL-STD-413 is suggested as a visual guide for inspecting O-rings.  Any major fault shall be rejected.  Major faults are defined by Table 4.2.

TABLE 4.2

| Quantitative Classification of Imperfections, Maximum Acceptable Dimensions (INCHES) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| O-Ring Cross-Sectional Width "W" | Backrind |  | Parting Line Indentations |  | Foreign Material |  | Parting Line Projection and Excessive Flash | Non-Fill |  | Mold Deposit Indentations |  | Flow Marks |  | Off-Register and/or Mismatch |
|  | Depth | Width | Depth | Width | Depth | Width | Max. Hgt. | Depth | Width | Depth | Width | Depth | Length | Max. |
| Less than 0.100 | 0 | 0 | 0.003 | 0.010 | 0 | 0 | 0.003 | 0 | 0 | 0.003 | 0.010 | 0.002 | 0.060 | 0.003 |
| 0.100 to 0.134 | 0.003 | 0.005 | 0.003 | 0.015 | 0.003 | 0.005 | 0.003 | 0.002 | 0.010 | 0.003 | 0.015 | 0.002 | 0.060 | 0.004 |
| 0.135 to 0.204 | 0.004 | 0.006 | 0.004 | 0.020 | 0.004 | 0.007 | 0.004 | 0.003 | 0.015 | 0.004 | 0.020 | 0.002 | 0.180 | 0.005 |
| 0.205 to 0.268 | 0.004 | 0.006 | 0.005 | 0.025 | 0.005 | 0.010 | 0.005 | 0.003 | 0.025 | 0.004 | 0.025 | 0.002 | 0.180 | 0.006 |
| 0.269 and over | 0.005 | 0.010 | 0.006 | 0.030 | 0.006 | 0.015 | 0.006 | 0.003 | 0.040 | 0.005 | 0.030 | 0.002 | 0.180 | 0.006 |

4.3 	Mold alignment shall produce mold flashing which does not exceed the allowable maximum shown on Sketches No. 1, 2, and 3.

4.4	Standard size O-rings shall have the actual cross section diameters shown per AS 568A rev 1974.

TABLE 5.4

For General Reference Purposes ONLY

| Nominal “W” | Actual “W” |
| --- | --- |
| 1/16” | .070” +/- .003” |
| 3/32” | .103” +/- .003” |
| 1/8” | .139” +/- .004” |
| 3/16” | .210” +/- .005” |
| 1/4” | .275” +/- .006” |

4.5	Standard size O-ring dimensions shall be specified by the nominal I.D., O.D. and nominal "W" cross sectional diameter in fractional sizes, and appropriate AS-568 Code Number.

  - Non-standard size O-rings shall be supplied to the size specified by the order.

5.    MARKING AND PACKAGING

5.1	Material identification marking of the rings shall be as follows unless otherwise specified on the particular part description.:

(a)  Rings molded of Neoprene shall be identified with Yellow marking

- Rings molded of Neoprene-1 shall be identified with an orange

marking.

(c)  Rings molded of Buna-N shall be identified with a Blue marking

(d)  Rings molded of Viton shall be identified with a Green marking.

(e)  Rings molded of Fluorel shall be identified with a Red marking.

(f)  Rings molded of HNBR shall be identified with a Purple marking.

5.2	The supplier shall place his appropriate identifying marking adjacent to the material identification marking as follows:

(a)  Goshen Rubber; two (2) White marks

(b)  Minnesota Rubber; one (1) White mark

(c)  Parker Seal; one (1) Gold mark

(d)  Parco: one (1) Gray mark

(e)  Stillman; two (2) Pink marks

(f)  Hercules; two (2) Gray marks

(g)  Acushnet Rubber; two (2) Gold marks

(h)  National O-Rings; one (1) Pink mark, marking is waived for

Viton rings supplied for YORK Part Numbers 028-04408-000,

028-04519-000, 028-10047-000 and 028-10838-000.

5.3	Material used for marking shall not affect the proper use of the ring. The marking material shall be of type applied after molding of ring.

5.4	The material and vendor identification marking on rings smaller than 5/16" I.D. is waived provided the rings are individually packed and full identification is on the package.

5.5	Each package shall contain rings of only one (1) manufacturing batch and each package shall be marked with the following data:

(a)  AS-568 Number

(b)  Cure date

(c)  Batch Number

(d)  Manufacturer's compound number

(e)  YORK Part Number

(f)  Material and Vendor identifying marking spelled out, i.e.

Blue - one Pink. (Required only for individually packed rings

per Paragraph 5.4).

6.	INSPECTION

6.1	At its option, YORK may inspect incoming shipments, using the specific gravity as the indication of compliance with this standard.  However, the supplier is responsible for full conformance with this standard without dependence on YORK inspection.

7.	APPROVED SOURCES OF SUPPLY AND SUPPLIER'S COMPOUND (see footnotes at bottom of table)

7.1   (a)        Goshen Rubber Company, Inc.   Compound       Specific Gravity

(1)  Neoprene                 1242                  1.49

(2)  Buna-N

(3)  Viton

(b)        Minnesota Rubber

(1)  Neoprene                 486 BV                1.42

(2)  Buna-N                   366Y                  1.30

‘’                      417FM                 1.22

‘’                      417GM                 1.26

(3)  Viton                    MRC514AD              1.89

(c)        Parker Seal Group

(1)  Neoprene                 C873-70               1.47

(2)  Buna-N                   N674-7                1.23

(3)  Viton                    V747-75               1.86

(4)  HNBR			     N1173-70              1.43

(d)        Parco Inc.

(1)  Neoprene	           3229-70***            1.37

‘’                    3110-70               1.45

(2)  Neoprene-1               3231-70               1.44

(3)  Buna-N                   4200-70               1.30

(4)  Viton                    9000-75               1.83

(5)  Fluorel (Parco Fluor)     994-75*              1.87

(6)  HNBR                     2269-70               1.28

(e)        Seals Eastern, Inc.

(1)  Neoprene

(2)  Buna-N                   5403                  1.24

(3)  Viton                    5763-70               1.92

(f)        Stillman Seal Division

(1)  Neoprene                 5040B-70              1.46

(2)  Buna-N                   SR310-70              1.23

(3)  Viton                    SR277-70              1.93

‘’                    SR2702-75              1.84

(g)        Hercules Products

(1)  Viton                    8262                  1.84

(h)        Acushnet Rubber Company, Inc.

(1)  Buna-N                   H14327                1.29

(i)        National O-rings

(1)  Neoprene-1               N-2-70                1.43

(2)  Buna-N                   B-46                  1.29

(3)  Viton                    V-14 (Black)          1.83

(4)  Viton                    V-35 (Brown)**        2.04

(5)  HNBR                     D-58                  1.19

*  Fluorel and Viton are both classified as Fluoro-elastomers but they shall not be interchanged unless so specified on the purchase order.

**  V-35 shall be supplied only when specified by the Purchase Order.

***  O-ring suppliers must review the Purchase Order Requirements carefully to determine if Parco Compound 3229-70 is acceptable.  Some York Part Number Descriptions specifically exclude the use of Parco Compound 3229-70.

- For vendors supplying both Neoprene and Neoprene-1 compounds, this specification permits the substitution of any Neoprene-1 compound for a Neoprene compound.

8.	PURCHASING

8.1  YORK Purchase Order shall specify:

(a)  Quantity

(b)  Size

(c)  AS Number

(d)  Type (O-Ring, Quad-Ring, or Quad-Bak Ring)

(e)  Material and Compound Number

(f)  YORK Part Number

(g)  YORK Standard R-807

9.	PART DESCRIPTION

9.1	Part description must specify the following:

(a)  Seal, O-Ring

(b)  Size

(c)  AS Number

(d)  Material:

(1)  Part description for reciprocating compressor shaft seal

applications must specify in addition to the material, the

compound and supplier.

(2)  Part description for Buna-N rings must specify "Lube

Treated" when special Molybdenum Disulfide processing for

low friction is required.

10.	CERTIFICATION

10.1	The following data shall be included with all certifications sent with the material.

(a)  Purchase Order Number

(b)  Item Number

(c)  Quantity

(d)  Part description, as indicated, on Purchase Order and/or

Industry Standards specified on drawings.

(e)  Part Number

(f)  Handwritten signature

(g)  Typed name of individual

(h)  Date

(i)  A statement of conformance that material conforms to the part

description.  This statement of conformance shall include:

[1]  Cure date

[2]  Expiration Date

[3]  Date of Shipment

[4]  Material Compound No.

[5]  Batch No.

[6]  Manufacturer of material supplied

11.	STORAGE INFORMATION

11.1	The age limitation of O-ring rubber compounds shall be as specified in SAE ARP 5316, latest issue revision shall apply.

11.2  Storage:

- Stock shall be handled on a FIFO "first in, first out" basis.

(b)  Seals shall be stored in their shipping packaging until installed

in equipment.

(c)  Storage conditions shall be as specified in SAE ARP 5316 Rev B.

11.3	Table 11.2 lists O-ring sizes which have been assigned an YORK Number.

- Some O-ring part numbers listed in Table 11.2 may be inactive. Check data base to determine if part number is active or must be loaded to the data base.

###### Table 11.2

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 001 CROSS SECTION DIAMETER 0.040 |  |  |  |  |  |  |  |
| 1/32 | 0.029 | 001 |  |  |  |  |  |
| 002 CROSS SECTION DIAMETER 0.050 |  |  |  |  |  |  |  |
| 3/64 | 0.042 | 002 |  |  |  |  |  |
| 003 CROSS SECTION DIAMETER 0.060 |  |  |  |  |  |  |  |
| 1/16 | 0.056 | 003 |  |  |  |  |  |
| 004-050 CROSS SECTION DIAMETER 0.070 |  |  |  |  |  |  |  |
| 5/64 | 0.070 | 004 |  |  |  |  |  |
| 3/32 | 0.101 | 005 |  |  |  |  |  |
| 1/8 | 0.114 | 006 | 028-10058-000 | 028-06895-000 |  |  |  |
| 5/32 | 0.145 | 007 |  | 028-09347-000 |  |  |  |
| 3/16 | 0.176 | 008 | 028-10156-000 | 028-11134-000 | 028-11997-000 | 028-11746-000 |  |
| 7/32 | 0.208 | 009 |  |  |  |  |  |
| 1/4 | 0.239 | 010 | 028-13772-000N | 028-08959-000 |  |  |  |
| 5/16 | 0.301 | 011 | 028-09378-000N |  | 028-12513-000 | 028-09373-000N |  |
| 3/8 | 0.364 | 012 | 028-08811-000 | 028-08116-000 | 028-11998-000 |  |  |
| 7/16 | 0.426 | 013 | 028-09383-000 | 028-12551-000 | 028-13060-000N | 028-09374-000 |  |
| 1/2 | 0.489 | 014 |  | 028-07809-000 |  |  |  |
| 9/16 | 0.551 | 015 | 028-08149-000 |  | 028-13061-000N | 028-09375-000N |  |
| 5/8 | 0.614 | 016 |  |  |  |  |  |
| 11/16 | 0.676 | 017 | 028-09471-000 |  | 028-13065-000N | 028-09376-000N |  |
|  |  |  |  |  | 028-13896-000 |  |  |
| 3/4 | 0.739 | 018 |  |  |  |  |  |
| 13/16 | 0.801 | 019 | 028-13436-000N |  | 028-13062-000N | 028-09377-000N |  |
| 7/8 | 0.864 | 020 |  | 028-04845-000 | 028-11188-000N | 028-06932-000 |  |
| 15/16 | 0.926 | 021 |  |  |  |  |  |
| 1 | 0.989 | 022 |  | 028-06764-000 | 028-13063-000N |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 004-050 CROSS SECTION DIAMETER 0.070 (Cont'd.) |  |  |  |  |  |  |  |
| 1 1/16 | 1.051 | 023 |  |  |  |  |  |
| 1 1/8 | 1.114 | 024 |  |  |  |  |  |
| 1 3/16 | 1.176 | 025 |  | 028-07872-000 |  |  |  |
| 1 1/4 | 1.239 | 026 |  |  |  |  |  |
| 1 5/16 | 1.301 | 027 |  |  |  |  |  |
| 1 3/8 | 1.364 | 028 |  |  |  |  |  |
| 1 1/2 | 1.489 | 029 |  |  | 028-13520-000N | 028-08270-000N |  |
| 1 5/8 | 1.614 | 030 |  |  |  |  |  |
| 1 3/4 | 1.739 | 031 |  |  | 028-14557-000N | 028-08269-000 |  |
| 1 7/8 | 1.864 | 032 |  |  |  |  |  |
| 2 | 1.989 | 033 |  |  |  |  |  |
| 2 1/8 | 2.114 | 034 |  |  |  |  |  |
| 2 1/4 | 2.239 | 035 |  | 028-07936-000 | 028-14443-000N |  |  |
| 2 3/8 | 2.364 | 036 |  |  |  |  |  |
| 2 1/2 | 2.489 | 037 |  |  |  |  |  |
| 2 5/8 | 2.614 | 038 |  |  |  |  |  |
| 2 3/4 | 2.739 | 039 |  |  |  |  |  |
| 2 7/8 | 2.864 | 040 |  |  | 028-14468-000 |  |  |
| 3 | 2.989 | 041 |  | 028-08394-000 | 028-11186-000N | 028-09561-000N |  |
| 3 1/4 | 3.239 | 042 | 028-08729-000 |  |  |  |  |
| 3 1/2 | 3.489 | 043 |  |  |  |  |  |
| 3 3/4 | 3.739 | 044 |  |  |  |  |  |
| 4 | 3.989 | 045 |  |  | 028-13898-000 |  |  |
| 4 1/4 | 4.239 | 046 |  |  | 028-14457-000N |  |  |
| 4 1/2 | 4.489 | 047 |  |  |  |  |  |
| 4 3/4 | 4.739 | 048 |  |  | 028-14447-000N |  |  |
| 5 | 4.989 | 049 |  |  |  |  |  |
| 5 1/4 | 5.239 | 050 |  |  |  |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 102-178 CROSS SECTION DIAMETER 0.103 |  |  |  |  |  |  |  |
| 1/16 | 0.049 | 102 |  |  |  |  |  |
| 3/32 | 0.081 | 103 |  |  |  |  |  |
| 1/8 | 0.112 | 104 |  |  |  |  |  |
| 5/32 | 0.143 | 105 |  |  |  |  |  |
| 3/16 | 0.174 | 106 |  |  |  |  |  |
| 7/32 | 0.206 | 107 |  |  |  |  |  |
| 1/4 | 0.237 | 108 |  |  |  |  |  |
| 5/16 | 0.299 | 109 | 028-13770-000N |  |  |  |  |
| 3/8 | 0.362 | 110 |  |  |  |  |  |
| 7/16 | 0.424 | 111 |  | 028-06729-000 | 028-14548-000N |  |  |
| 1/2 | 0.487 | 112 |  |  |  |  |  |
| 9/16 | 0.549 | 113 |  | 028-03292-000 |  | 028-03657-000N |  |
| 5/8 | 0.612 | 114 | 028-04665-000 | 028-04662-000 | 028-11999-000 |  |  |
| 11/16 | 0.674 | 115 |  |  |  | 028-05404-000 |  |
| 3/4 | 0.737 | 116 |  | 028-14435-000 | 028-14549-000N |  |  |
| 13/16 | 0.799 | 117 |  |  |  |  |  |
| 7/8 | 0.862 | 118 |  |  |  |  |  |
| 15/16 | 0.924 | 119 | 028-06831-000 |  |  | 028-05403-000N |  |
| 1 | 0.987 | 120 |  |  |  |  |  |
| 1 1/16 | 1.049 | 121 | 028-06832-000 | 028-04754-000 | 028-13717-000N |  |  |
| 1 1/8 | 1.112 | 122 |  | 028-06937-000 |  |  |  |
| 1 3/16 | 1.174 | 123 | 028-06933-000 |  | 028-13426-000N |  |  |
| 1 1/4 | 1.237 | 124 |  |  |  |  |  |
| 1 5/16 | 1.299 | 125 | 028-06834-000 | 028-06791-000 | 028-13701-000 | 028-10026-000 |  |
| 1 3/8 | 1.362 | 126 |  | 028-06838-000 |  |  |  |
| 1 7/16 | 1.424 | 127 | 028-06835-000 | 028-10964-000 | 028-13064-000N |  |  |
| 1 1/2 | 1.487 | 128 |  | 028-08131-000 | 028-11192-000N | 028-04479-000 |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 102-178 CROSS SECTION DIAMETER 0.103 (Cont'd) |  |  |  |  |  |  |  |
| 1 9/16 | 1.549 | 129 |  |  |  |  |  |
| 1 5/8 | 1.612 | 130 |  |  |  |  |  |
| 1 11/16 | 1.674 | 131 |  |  |  |  |  |
| 1 3/4 | 1.737 | 132 |  |  | 028-06839-000 |  |  |
| 1 13/16 | 1.799 | 133 | 028-07998-000 | 028-08294-000 | 028-12997-000N | 028-07407-000N |  |
| 1 7/8 | 1.862 | 134 |  |  |  |  |  |
| 1 15/16 | 1.925 | 135 |  |  |  |  |  |
| 2 | 1.987 | 136 |  |  | 028-14419-000 |  |  |
| 2 1/16 | 2.050 | 137 |  | 028-07938-000N |  |  |  |
| 2 1/8 | 2.112 | 138 |  |  |  |  |  |
| 2 3/16 | 2.175 | 139 |  |  |  |  |  |
| 2 1/4 | 2.237 | 140 |  |  |  |  |  |
| 2 5/16 | 2.300 | 141 |  |  |  |  |  |
| 2 3/8 | 2.362 | 142 |  |  |  |  |  |
| 2 7/16 | 2.425 | 143 | 028-09292-000 |  |  | 028-10023-000 |  |
| 2 1/2 | 2.487 | 144 |  |  |  |  |  |
| 2 9/16 | 2.550 | 145 |  | 028-11976-000 |  |  |  |
| 2 5/8 | 2.612 | 146 |  |  |  |  |  |
| 2 11/16 | 2.675 | 147 | 028-09966-000 |  |  | 028-10046-000 |  |
| 2 3/4 | 2.737 | 148 |  |  |  | 028-09293-000 |  |
| 2 13/16 | 2.800 | 149 |  |  |  |  |  |
| 2 7/8 | 2.862 | 150 |  |  | 028-12943-000N |  |  |
| 3 | 2.987 | 151 |  |  |  |  |  |
| 3 1/4 | 3.237 | 152 |  |  | 028-14420-000 |  |  |
| 3 1/2 | 3.487 | 153 |  |  | 028-15082-000 |  |  |
| 3 3/4 | 3.737 | 154 |  | 028-15074-000 |  |  |  |
| 4 | 3.987 | 155 |  |  |  |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 102-178 CROSS SECTION DIAMETER 0.103 (Cont'd.) |  |  |  |  |  |  |  |
| 4 1/4 | 4.237 | 156 |  |  |  |  |  |
| 4 1/2 | 4.487 | 157 |  |  |  |  |  |
| 4 3/4 | 4.737 | 158 |  |  |  |  |  |
| 5 | 4.987 | 159 |  |  |  |  |  |
| 5 1/4 | 5.237 | 160 |  |  | 028-14403-000 |  |  |
| 5 1/2 | 5.487 | 161 |  |  | 028-14446-000N |  |  |
| 5 3/4 | 5.737 | 162 |  | 028-13870-000 |  |  |  |
| 6 | 5.987 | 163 |  |  |  |  |  |
| 6 1/4 | 6.237 | 164 |  |  |  |  |  |
| 6 1/2 | 6.487 | 165 |  |  |  |  |  |
| 6 3/4 | 6.737 | 166 |  |  |  |  |  |
| 7 | 6.987 | 167 |  |  | 028-14445-000N |  |  |
| 7 1/4 | 7.237 | 168 |  |  | 028-13528-000N |  |  |
| 7 1/2 | 7.487 | 169 |  |  |  |  |  |
| 7 3/4 | 7.737 | 170 |  |  |  |  |  |
| 8 | 7.987 | 171 |  |  |  |  |  |
| 8 1/4 | 8.237 | 172 |  |  |  |  |  |
| 8 1/2 | 8.487 | 173 |  |  |  |  |  |
| 8 3/4 | 8.737 | 174 |  |  |  |  |  |
| 9 | 8.987 | 175 |  |  |  |  |  |
| 9 1/4 | 9.237 | 176 |  |  |  |  |  |
| 9 1/2 | 9.487 | 177 |  |  |  |  |  |
| 9 3/4 | 9.737 | 178 |  |  |  |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 201-284 CROSS SECTION DIAMETER 0.139 |  |  |  |  |  |  |  |
| 3/16 | 0.171 | 201 |  |  |  |  |  |
| 1/4 | 0.234 | 202 |  |  |  |  |  |
| 5/16 | 0.296 | 203 |  |  |  |  |  |
| 3/8 | 0.359 | 204 |  |  |  |  |  |
| 7/16 | 0.421 | 205 |  |  |  |  |  |
| 1/2 | 0.484 | 206 |  |  |  |  |  |
| 9/16 | 0.546 | 207 |  |  |  |  |  |
| 5/8 | 0.609 | 208 |  |  |  |  |  |
| 11/16 | 0.671 | 209 |  |  |  |  |  |
| 3/4 | 0.734 | 210 | 028-04666-000 | 028-03282-000 |  |  |  |
| 13/16 | 0.796 | 211 |  |  |  |  |  |
| 7/8 | 0.859 | 212 | 028-04930-000 |  |  | 028-07761-000 |  |
| 15/16 | 0.921 | 213 | 028-04668-000 | 028-04664-000 | 028-13975-000 |  |  |
| 1 | 0.984 | 214 | 028-09309-000 | 028-03516-000 | 028-12201-000 | 028-04522-000 |  |
| 1 1/16 | 1.046 | 215 |  |  |  |  |  |
| 1 1/8 | 1.109 | 216 | 028-07002-000 | 028-03838-000 | 028-12200-000 | 028-04353-000N |  |
| 1 3/16 | 1.171 | 217 | 028-11430-000N |  |  |  |  |
| 1 1/4 | 1.234 | 218 | 028-05189-000 | 028-05181-000 | 028-12922-000N |  |  |
| 1 5/16 | 1.296 | 219 |  | 028-12552-000 | 028-12920-000N |  |  |
| 1 3/8 | 1.359 | 220 | 028-08633-000* | 028-03027-000 | 028-11190-000N | 028-04408-000N** |  |
| 1 7/16 | 1.421 | 221 | 028-08831-000N |  |  |  |  |
| 1 1/2 | 1.484 | 222 | 028-05164-000 | 028-05410-000N | 028-13071-000N |  |  |
| 1 5/8 | 1.609 | 223 |  | 028-10576-000 | 028-11187-000N | 028-04861-000 |  |
| 1 3/4 | 1.734 | 224 | 028-08640-000* | 028-05188-000 | 028-12998-000N | 028-04348-000N |  |
|  |  |  | 028-05196-000 |  |  |  |  |
| 1 7/8 | 1.859 | 225 |  | 028-11923-000 |  |  |  |
| 2 | 1.984 | 226 | 028-08970-000 | 028-03236-000 |  |  | 028-15292-000 |
| 2 1/8 | 2.109 | 227 | 028-08622-000* | 028-08681-000 | 028-13512-000N | 028-04478-000 |  |
| 2 1/4 | 2.234 | 228 |  | 028-03803-000 |  |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 201-284 CROSS SECTION DIAMETER 0.139 (Cont'd.) |  |  |  |  |  |  |  |
| 2 3/8 | 2.359 | 229 |  |  |  |  |  |
| 2 1/2 | 2.484 | 230 |  | 028-03029-000 |  |  |  |
| 2 5/8 | 2.609 | 231 |  | 028-12965-000 | 028-14495-000 |  |  |
|  |  |  |  |  | 028-13144-000N |  |  |
| 2 3/4 | 2.734 | 232 |  | 028-05166-000 | 028-13578-000 |  |  |
|  |  |  |  |  | 028-13713-000N |  |  |
| 2 7/8 | 2.859 | 233 | 028-08971-000 | 028-11193-000N |  |  |  |
| 3 | 2.984 | 234 |  |  | 028-13519-000N 028-07198-000 | 028-04606-000N |  |
| 3 1/8 | 3.109 | 235 |  |  | 028-13923-000 |  |  |
|  |  |  |  |  | 028-12938-000N |  |  |
| 3 1/4 | 3.234 | 236 |  | 028-11903-000 | 028-11189-000N | 028-04409-000N |  |
| 3 3/8 | 3.359 | 237 |  |  |  |  |  |
| 3 1/2 | 3.484 | 238 |  | 028-05173-000 | 028-14404-000 |  |  |
| 3 5/8 | 3.609 | 239 |  |  | 028-12996-000N | 028-09562-000N |  |
| 3 3/4 | 3.734 | 240 |  |  | 028-12925-000N | 028-07901-000N |  |
| 3 7/8 | 3.859 | 241 | 028-13068-000 | 028-08299-000 | 028-12208-000 | 028-04352-000N |  |
| 4 | 3.984 | 242 | 028-13067-000 | 028-03878-000 | 028-12210-000 | 028-04349-000N |  |
| 4 1/8 | 4.109 | 243 | 028-11940-000 |  | 028-12205-000 |  |  |
| 4 1/4 | 4.234 | 244 |  | 028-12259-000 | 028-13125-000N |  |  |
| 4 3/8 | 4.359 | 245 |  | 028-06788-000 | 028-13111-000N | 028-04639-000N |  |
| 4 1/2 | 4.484 | 246 | 028-09294-000 |  |  | 028-10024-000N |  |
| 4 5/8 | 4.609 | 247 | 028-10158-000 |  | 028-12202-000 |  |  |
| 4 3/4 | 4.734 | 248 |  |  | 028-13536-000N | 028-09577-000 |  |
| 4 7/8 | 4.859 | 249 | 028-11939-000 | 028-12225-000 | 028-12207-000 | 028-08848-000N |  |
| 5 | 4.984 | 250 | 028-10571-000 |  | 028-12211-000N | 028-04517-000 |  |
| 5 1/8 | 5.109 | 251 |  |  | 028-13169-000N | 028-13026-000N |  |
| 5 1/4 | 5.234 | 252 |  |  | 028-14449-000N |  |  |
| 5 3/8 | 5.359 | 253 | 028-10837-000 | 028-11975-000 | 028-12203-000 |  |  |
| 5 1/2 | 5.484 | 254 |  | 028-11978-000 |  |  |  |
| 5 5/8 | 5.609 | 255 |  | 028-12258-000 |  |  |  |
| 5 3/4 | 5.734 | 256 |  |  | 028-14555-000N |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 201-284 CROSS SECTION DIAMETER 0.139 (Cont'd.) |  |  |  |  |  |  |  |
| 5 7/8 | 5.859 | 257 | 028-10836-000 |  | 028-12204-000 |  |  |
| 6 | 5.984 | 258 |  |  | 028-14405-000 |  |  |
| 6 1/4 | 6.234 | 259 |  |  |  |  |  |
| 6 1/2 | 6.484 | 260 |  | 028-12224-000 | 028-12939-000N |  |  |
| 6 3/4 | 6.734 | 261 |  |  |  |  |  |
| 7 | 6.984 | 262 |  | 028-12550-000 | 028-12923-000N |  |  |
| 7 1/4 | 7.234 | 263 |  |  | 028-13130-000N |  |  |
| 7 1/2 | 7.484 | 264 |  | 028-12713-000 |  |  |  |
| 7 3/4 | 7.734 | 265 | 028-11941-000 | 028-12256-000 | 028-12206-000 | 028-04679-000 |  |
| 8 | 7.984 | 266 | 028-11409-000 | 028-12255-000 | 028-13123-000N |  |  |
| 8 1/4 | 8.234 | 267 | 028-03234-000 | 028-05409-000 | 028-12993-000N |  |  |
|  |  |  |  |  | 028-15078-000 |  |  |
|  |  |  |  |  | 028-13165-000N |  |  |
| 8 1/2 | 8.484 | 268 | 028-03587-000 | 028-12902-000 |  |  |  |
| 8 3/4 | 8.734 | 269 |  |  | 028-12945-000N |  |  |
| 9 | 8.984 | 270 |  |  | 028-14508-000 |  |  |
| 9 1/4 | 9.234 | 271 |  | 028-04696-000 |  |  |  |
| 9 1/2 | 9.484 | 272 |  |  | 028-12946-000N |  |  |
| 9 3/4 | 9.734 | 273 |  | 028-07931-000 |  |  |  |
| 10 | 9.984 | 274 |  | 028-12247-000 | 028-12994-000N |  |  |
| 10 1/2 | 10.484 | 275 |  | 028-12226-000 |  |  |  |
| 11 | 10.984 | 276 |  |  | 028-13514-000N |  |  |
| 11 1/2 | 11.484 | 277 |  | 028-12567-000 | 028-13977-000 |  |  |
| 12 | 11.984 | 278 | 028-13773-000N | 028-12568-000 | 028-14411-000 |  |  |
| 13 | 12.984 | 279 |  |  | 028-14412-000 |  |  |
| 14 | 13.984 | 280 |  |  | 028-14454-000N |  |  |
| 15 | 14.984 | 281 |  |  |  |  | 028-15063-000 |
| 16 | 15.955 | 282 |  |  | 028-13525-000N | 028-10371-000N |  |
| 17 | 16.955 | 283 |  |  | 028-12928-000N |  |  |
| 18 | 17.955 | 284 |  | 028-12257-000 |  |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 309-395 CROSS SECTION DIAMETER 0.210 |  |  |  |  |  |  |  |
| 7/16 | 0.412 | 309 |  |  |  |  |  |
| 1/2 | 0.475 | 310 |  |  |  |  |  |
| 9/16 | 0.537 | 311 |  |  |  |  |  |
| 5/8 | 0.600 | 312 |  |  |  |  |  |
| 11/16 | 0.662 | 313 |  |  |  |  |  |
| 3/4 | 0.725 | 314 |  |  |  |  |  |
| 13/16 | 0.787 | 315 |  |  |  |  |  |
| 7/8 | 0.850 | 316 |  |  |  |  |  |
| 15/16 | 0.912 | 317 |  |  |  |  |  |
| 1 | 0.975 | 318 |  |  |  |  |  |
| 1 1/16 | 1.037 | 319 |  |  |  |  |  |
| 1 1/8 | 1.100 | 320 |  |  |  |  |  |
| 1 3/16 | 1.162 | 321 |  |  |  |  |  |
| 1 1/4 | 1.225 | 322 |  |  |  |  |  |
| 1 5/16 | 1.287 | 323 |  |  |  |  |  |
| 1 3/8 | 1.350 | 324 |  |  | 028-13046-000N |  |  |
| 1 1/2 | 1.475 | 325 |  |  |  |  |  |
| 1 5/8 | 1.600 | 326 | 028-05195-000 | 028-05183-000 |  |  |  |
| 1 3/4 | 1.725 | 327 |  | 028-10997-000 |  | 028-09306-000 |  |
| 1 7/8 | 1.850 | 328 |  |  | 028-12926-000N |  |  |
| 2 | 1.975 | 329 | 028-05190-000 | 028-05182-000 |  |  |  |
| 2 1/8 | 2.100 | 330 | 028-03788-000 | 028—03517-000 | 028-13513-000N | 028-04519-000** |  |
| 2 1/4 | 2.225 | 331 | 028-05193-000 | 028-08125-000 |  |  |  |
| 2 3/8 | 2.350 | 332 |  |  |  |  |  |
| 2 1/2 | 2.475 | 333 |  |  | 028-13099-000N |  |  |
| 2 5/8 | 2.600 | 334 | 028-08638-000* | 028-05184-000 | 028-14469-000 | 028-10047-000** |  |
|  |  |  | 028-05194-000 |  |  |  |  |
| 2 3/4 | 2.775 | 335 |  | 028-03241-000 | 028-12941-000N |  |  |
| 2 7/8 | 2.850 | 336 |  | 028-07420-000 |  |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 309-395 CROSS SECTION DIAMETER 0.210 (Cont'd.) |  |  |  |  |  |  |  |
| 3 | 2.975 | 337 | 028-03167-000 | 028-03164-000 | 028-13096-000N |  |  |
| 3 1/8 | 3.100 | 338 |  |  | 028-12597-000 |  |  |
| 3 1/4 | 3.225 | 339 | 028-05163-000 | 028-03840-000 | 028-13097-000N |  |  |
| 3 3/8 | 3.350 | 340 | 028-08626-000* | 028-03739-000 | 028-13704-000 | 028-10838-000** |  |
| 3 1/2 | 3.475 | 341 | 028-05191-000 | 028-05187-000 |  |  |  |
| 3 5/8 | 3.600 | 342 | 028-03166-000 | 028-03165-000 |  |  |  |
| 3 3/4 | 3.725 | 343 |  |  |  |  |  |
| 3 7/8 | 3.850 | 344 |  |  |  |  |  |
| 4 | 3.975 | 345 |  |  | 028-12927-000N |  |  |
| 4 1/8 | 4.100 | 346 | 028-05192-000 | 028-05186-000 |  |  |  |
| 4 1/4 | 4.225 | 347 | 028-08637-000* | 028-04825-000 | 028-13035-000N | 028-07685-000 |  |
| 4 3/8 | 4.350 | 348 |  |  |  |  |  |
| 4 1/2 | 4.475 | 349 |  |  |  |  |  |
| 4 5/8 | 4.600 | 350 |  |  |  |  |  |
| 4 3/4 | 4.725 | 351 |  |  |  |  |  |
| 4 7/8 | 4.850 | 352 |  |  |  |  |  |
| 5 | 4.975 | 353 |  |  | 028-13461-000N |  |  |
| 5 1/8 | 5.100 | 354 |  |  |  |  |  |
| 5 1/4 | 5.225 | 355 |  |  |  |  |  |
| 5 3/8 | 5.350 | 356 |  |  |  |  |  |
| 5 1/2 | 5.475 | 357 |  |  |  |  |  |
| 5 5/8 | 5.600 | 358 |  | 028-09305-000 |  |  |  |
| 5 3/4 | 5.725 | 359 |  |  |  |  |  |
| 5 7/8 | 5.850 | 360 |  |  | 028-15318-000 |  |  |
| 6 | 5.975 | 361 |  |  | 028-14482-000 |  |  |
| 6 1/4 | 6.225 | 362 |  |  |  |  |  |
| 6 1/2 | 6.475 | 363 |  |  | 028-13042-000N |  |  |
| 6 3/4 | 6.725 | 364 |  |  |  |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 309-395 CROSS SECTION DIAMETER 0.210 (Cont'd.) |  |  |  |  |  |  |  |
| 7 | 6.975 | 365 |  |  | 028-13051-000N |  |  |
| 7 1/4 | 7.225 | 366 | 028-13032-000 |  |  |  |  |
| 7 1/2 | 7.475 | 367 |  |  | 028-15061-000 |  |  |
| 7 3/4 | 7.725 | 368 |  |  |  |  |  |
| 8 | 7.975 | 369 |  |  |  |  |  |
| 8 1/4 | 8.225 | 370 |  |  |  |  |  |
| 8 1/2 | 8.475 | 371 |  |  |  |  |  |
| 8 3/4 | 8.725 | 372 |  |  | 028-13131-000N |  |  |
| 9 | 8.975 | 373 |  |  | 028-13458-000N |  |  |
| 9 1/4 | 9.225 | 374 |  |  |  |  |  |
| 9 1/2 | 9.475 | 375 |  |  | 028-15319-000 |  |  |
| 9 3/4 | 9.725 | 376 |  |  |  |  |  |
| 10 | 9.975 | 377 |  |  |  |  |  |
| 10 1/2 | 10.475 | 378 |  |  |  |  |  |
| 11 | 10.975 | 379 |  |  |  |  |  |
| 11 1/2 | 11.475 | 380 |  |  | 028-14464-000N |  |  |
| 12 | 11.975 | 381 |  |  |  |  |  |
| 13 | 12.975 | 382 |  |  |  |  |  |
| 14 | 13.975 | 383 |  |  |  |  |  |
| 15 | 14.975 | 384 |  |  |  |  |  |
| 16 | 15.995 | 385 |  |  |  |  |  |
| 17 | 16.995 | 386 |  |  |  |  |  |
| 18 | 17.995 | 387 |  |  |  |  |  |
| 19 | 18.953 | 388 |  |  | 028-13135-000N |  |  |
| 20 | 19.953 | 389 |  |  | 028-14413-000 |  |  |
| 21 | 20.953 | 390 |  |  |  |  |  |
| 22 | 21.953 | 391 |  |  | 028-12991-000N |  |  |
| 23 | 22.940 | 392 |  |  |  |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 309-395 CROSS SECTION DIAMETER 0.210 (Cont'd.) |  |  |  |  |  |  |  |
| 24 | 23.940 | 393 |  |  | 028-13175-000N |  |  |
| 25 | 24.940 | 394 |  |  | 028-13041-000N |  |  |
| 26 | 25.940 | 395 |  |  | 028-13176-000N |  |  |
| 425-475 CROSS SECTION DIAMETER 0.275 |  |  |  |  |  |  |  |
| 4 1/2 | 4.475 | 425 |  |  |  |  |  |
| 4 5/8 | 4.600 | 426 |  |  |  |  |  |
| 4 3/4 | 4.725 | 427 |  |  |  |  |  |
| 4 7/8 | 4.850 | 428 |  |  |  |  |  |
| 5 | 4.975 | 429 | 028-03796-000 | 028-04401-000 |  |  |  |
| 5 1/8 | 5.100 | 430 |  |  | 028-12937-000N |  |  |
| 5 1/4 | 5.225 | 431 |  |  |  |  |  |
| 5 3/8 | 5.350 | 432 | 028-08630-000* | 028-07970-000 | 028-13706-000 |  |  |
| 5 1/2 | 5.475 | 433 |  |  |  |  |  |
| 5 5/8 | 5.600 | 434 |  |  |  |  |  |
| 5 3/4 | 5.725 | 435 |  |  |  |  |  |
| 5 7/8 | 5.850 | 436 |  |  |  |  |  |
| 6 | 5.975 | 437 |  |  |  |  |  |
| 6 1/4 | 5.225 | 438 |  |  |  |  |  |
| 6 1/2 | 6.475 | 439 |  |  | 028-13484-000N |  |  |
| 6 3/4 | 6.725 | 440 |  |  |  |  |  |
| 7 | 6.975 | 441 |  |  |  |  |  |
| 7 1/4 | 7.225 | 442 |  |  |  |  |  |
| 7 1/2 | 7.475 | 443 |  |  |  |  |  |
| 7 3/4 | 7.725 | 444 |  |  |  |  |  |
| 8 | 7.975 | 445 |  |  |  |  |  |
| 8 1/2 | 8.475 | 446 |  |  |  |  |  |
| 9 | 8.975 | 447 |  |  |  |  |  |
| 9 1/2 | 9.475 | 448 |  |  | 028-13093-000N |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 425-475 CROSS SECTION DIAMETER 0.275 (Cont'd.) |  |  |  |  |  |  |  |
| 10 | 9.975 | 449 | 028-09295-000 |  |  | 028—10025-000 |  |
| 10 1/2 | 10.475 | 450 |  | 028-03856-000 | 028-13168-000N |  |  |
| 11 | 10.975 | 451 |  |  |  |  |  |
| 11 1/2 | 11.475 | 452 |  |  | 028-12942-000N |  |  |
| 12 | 11.975 | 453 |  |  |  |  |  |
| 12 1/2 | 12.475 | 454 |  |  |  |  |  |
| 13 | 12.975 | 455 |  | 028-03855-000 |  |  |  |
| 13 1/2 | 13.475 | 456 |  | 028-11977-000 |  |  |  |
| 14 | 13.975 | 457 |  |  |  |  |  |
| 14 1/2 | 14.475 | 458 |  |  | 028-11191-000N |  |  |
| 15 | 14.975 | 459 |  |  |  |  |  |
| 15 1/2 | 15.475 | 460 |  |  | 028-13094-000N | 028-13754-000 |  |
| 16 | 15.955 | 461 |  |  |  |  |  |
| 16 1/2 | 16.455 | 462 |  |  |  |  |  |
| 17 | 16.955 | 463 |  |  |  |  |  |
| 17 1/2 | 17.455 | 464 |  |  |  |  |  |
| 18 | 17.955 | 465 |  |  |  |  |  |
| 18 1/2 | 18.455 | 466 |  |  |  |  |  |
| 19 | 18.955 | 467 |  |  | 028-14414-000 |  |  |
| 19 1/2 | 19.455 | 468 | 028-09432-000 | 028-08297-000 |  | 028-05401-000N |  |
| 20 | 19.955 | 469 | 028-10557-000 |  |  |  |  |
| 21 | 20.955 | 470 |  |  |  |  |  |
| 22 | 21.955 | 471 |  |  | 028-14406-000 | 028-11974-000N |  |
| 23 | 22.940 | 472 |  |  |  |  |  |
| 24 | 23.940 | 473 |  |  |  |  |  |
| 25 | 24.940 | 474 |  |  |  |  |  |
| 26 | 25.940 | 475 |  |  |  |  |  |

| NOM. | ACT. | AS568 | YORK PART NUMBER *** |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| I.D. | I.D. | DASH | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  |  | NUMBER |  |  |  |  |  |
| 901 CROSS SECTION DIAMETER 0.056 |  |  |  |  |  |  |  |
| 3/32 | 0.185 | 901 |  |  |  |  |  |
| 902-903 CROSS SECTION DIAMETER 0.065 |  |  |  |  |  |  |  |
| 1/8 | 0.239 | 902 |  |  |  |  |  |
| 3/16 | 0.301 | 903 |  | 028-11198-000 | 028-12209-000 | 028-07519-000N |  |
| 904-905 CROSS SECTION DIAMETER 0.072 |  |  |  |  |  |  |  |
| 1/4 | 0.351 | 904 | 028-08012-000N |  | 028-13056-000N | 028-07442-000 |  |
|  |  |  |  |  | 028-13832-000 |  |  |
| 5/16 | 0.414 | 905 |  |  |  |  |  |
| 906 CROSS SECTION DIAMETER 0.078 |  |  |  |  |  |  |  |
| 3/8 | 0.468 | 906 | 028-07759-000N | 028-11462-000N | 028-11195-000N | 028-07422-000N |  |
| 907 CROSS SECTION DIAMETER 0.082 |  |  |  |  |  |  |  |
| 7/16 | 0.530 | 907 |  |  |  |  |  |
| 908 CROSS SECTION DIAMETER 0.087 |  |  |  |  |  |  |  |
| 1/2 | 0.644 | 908 | 029-08035-000N | 028-07937-000 | 028-13057-000N | 028-07443-000N |  |
|  |  |  |  |  | 028-12919-000N |  |  |
| 909-910 CROSS SECTION DIAMETER 0.097 |  |  |  |  |  |  |  |
| 9/16 | 0.706 | 909 |  |  |  |  |  |
| 5/8 | 0.755 | 910 | 028-08282-000N |  | 028-13066-000N | 028-07524-000N |  |
| 911-918 CROSS SECTION DIAMETER 0.116 |  |  |  |  |  |  |  |
| 11/16 | 0.863 | 911 |  |  |  |  |  |
| 3/4 | 0.924 | 912 | 028-07848-000N |  | 028-11194-000N | 028-07431-000N |  |
| 13/16 | 0.986 | 913 |  |  |  |  |  |
| 7/8 | 1.047 | 914 |  |  | 028-13563-000 | 028-07497-000 |  |
| 1 | 1.171 | 916 | 028-08259-000N |  | 028-13058-000N | 028-07828-000 |  |
|  |  |  |  |  | 028-12918-000N |  |  |
| 1 1/8 | 1.355 | 918 |  |  |  |  |  |
| 920-932 CROSS SECTION DIAMETER 0.118 |  |  |  |  |  |  |  |
| 1 1/4 | 1.475 | 920 |  |  | 028-13070-000N | 028-07457-000 |  |
| 1 1/2 | 1.720 | 924 |  |  | 028-13059-000N | 028-07453-000N |  |
|  |  |  |  |  | 028-13160-000N |  |  |
| 1 3/4 | 2.090 | 928 |  |  |  |  |  |
| 2 | 2.337 | 932 |  |  | 028-13709-000N | 028-08708-000N |  |

| NON STANDARD SIZES |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| NOM. | ACT. | YORK PART NUMBER |  |  |  |  |  |
| I.D. | I.D. |  | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
| CROSS SECTION DIAMETER 0.070 |  |  |  |  |  |  |  |
|  | 5.340 |  | 028-10157-000N |  | 028-13777-000 |  |  |
| CROSS SECTION DIAMETER 0.103 |  |  |  |  |  |  |  |
|  | 4.819 |  |  |  | 028-13500-000N |  |  |
| CROSS SECTION DIAMETER 0.139 |  |  |  |  |  |  |  |
|  | 6.792 |  |  |  | 028-12931-000N |  |  |
|  | 14.759 |  |  |  | 028-13184-000N |  |  |
|  | 17.722 |  |  |  | 028-12213-000 |  |  |
|  | 17.775 |  |  |  | 028-13934-000N |  |  |
|  | 23.940 |  |  |  | 028-13981-000N |  |  |
|  | 24.605 |  |  |  | 028-12930-000N |  |  |
| CROSS SECTION DIAMETER 0.210 |  |  |  |  |  |  |  |
|  | 18.450 |  |  |  | 028-13526-000N |  |  |
|  | 23.440 |  |  |  | 028-12951-000N |  |  |
|  | 23.440 |  |  |  | 028-13142-000N |  |  |
|  | 26.969 |  |  |  | 028-13515-000N |  |  |
|  | 28.615 |  |  |  | 028-13541-000N |  |  |
|  | 29.095 |  |  |  | 028-13129-000N |  |  |
|  | 29.615 |  |  |  | 028-13527-000N |  |  |
| CROSS SECTION DIAMETER 0.275 |  |  |  |  |  |  |  |
| 8 3/4 |  |  |  |  | 028-04501-000 |  |  |
|  | 9.748 |  |  |  | 028-13138-000N |  |  |
|  | 21.550 |  |  |  | 028-12929-000N |  |  |
|  | 25.440 |  |  |  | 028-13134-000N |  |  |
|  | 26.455 |  |  |  | 028-13935-000N |  |  |
|  | 26.623 |  |  |  | 028-13846-000 |  |  |
|  | 26.840 |  |  |  | 028-12924-000N |  |  |
|  | 31.440 |  |  |  | 028-12992-000N |  |  |
|  | 31.906 |  |  |  | 028-13163-000N |  |  |

| NON STANDARD SIZES |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CROSS SECTION DIAMETER 0.275 (Cont’d.) |  |  |  |  |  |  |  |
| NOM. | ACT. | YORK PART NUMBER |  |  |  |  |  |
| I.D. | I.D. |  | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  | ACT. |  | YORK PART NUMBER |  |  |  |  |
|  | I.D. |  | BUNA-N | NEOPRENE | NEOPRENE-1 | VITON | HNBR |
|  | 35.3 |  |  |  | 028-13166-000N |  |  |
|  | 35.94 |  |  |  | 028-13516-000N |  |  |
|  | 37.050 |  |  |  | 028-15083-000 |  |  |

*   “Lube Treated” Special processing for reduced friction.

**  When these Viton O-rings are supplied by National O-Rings they shall

be compound V-35 (brown).

*** Some part numbers may be inactive.  Check data base to determine if part

number is active or must be loaded to the data base.

N - Marine, Military & Government Part.