## JCI-YORK 6-9-10
SANDRIDGE CENTURY PROJECT TRAIN 1
| JOHNSON CONTROLS INC- YORK COMPRESSORS DAILEY REPORT |  |  |  |  | DATE: 6/ 25 /10
REPORT BY: |  | Jerry Kirwan |  |  |  | REV. 0 | BJ
NAMES |  |  | WORK TYPE: (CHECK ONE) |  | INSTALLATION | WARRANTY
CREW CHIEF: | JERRY KIRWAN |  |  | C-1231A | X
PROGRAMMER: | JOE TORO |  |  | C-1231B | X
MECHANIC: |  |  |  | C-1231C | X
MECHANIC: |  |  |  | C-1231D | X
MECHANIC: |  |  |  | C-1231E | X
MECHANIC: |  |  |  | C-1231F | X
Equipment # | Checklists/ Field Findings |  |  |  |  | Status
C-1231A | N2 purge @ 0 psi - Unit open for work - |  |  |  |  | COMPLETE
| Axial Spacing check |  |  |  |  | PENDING
| 480 VT power - Transformer connection correction |  |  |  |  | COMPLETE
| Transmitter(s) - Re-install |  |  |  |  | PENDING
| Rotation check of Compressor & Gear Oil pumps |  |  |  |  | COMPLETE
| Preperation of package for DCS Loop testing |  |  |  |  | STARTED
| Copressor Sump Oil Change out as previously agreed upon |  |  |  |  | PENDING
| XV-1231A4 LCD issue may be corrected (Reavaluate fix on 6/26) |  |  |  |  | PENDING
C-1231B | N2 purge @ 0 psi - Unit open for work - |  |  |  |  | NOT OK
| Copressor Sump Oil Change out as previously agreed upon |  |  |  |  | PENDING
| Preperation of package for DCS Loop testing |  |  |  |  | STARTED
| Fiber-optic connections |  |  |  |  | COMPLETE
| 480 VT power - Transformer connection correction |  |  |  |  | COMPLETE
C-1231C | N2 purge @ 0 psi - Unit open for work - |  |  |  |  | NOT OK
| Fiber-optic connections |  |  |  |  | COMPLETE
| 480 VT power - Transformer connection correction |  |  |  |  | PENDING
| Transmitter(s) - Re-install |  |  |  |  | COMPLETE
| Copressor Sump Oil Change out as previously agreed upon |  |  |  |  | PENDING
| Reloaded PLC with GE Multilin signal inversion |  |  |  |  | COMPLETE
C-1231D | N2 purge @ 8 psi (needs reavaluated) |  |  |  |  | PENDING
| Copressor Sump Oil Change out as previously agreed upon |  |  |  |  | PENDING
| Fiber-optic connections |  |  |  |  | COMPLETE
| 480 VT power - Transformer connection correction |  |  |  |  | PENDING
| Transmitter(s) - Re-install |  |  |  |  | PENDING
C-1231E | N2 purge @ 0 psi - Unit open for work - |  |  |  |  | PENDING
| Interconnecting Piping - re-install |  |  |  |  | Started
| Fiber-optic connections (Test HMI that was not communicating) |  |  |  |  | PENDING
| 480 VT power - Transformer connection correction |  |  |  |  | PENDING
| Transmitter(s) - Re-install |  |  |  |  | PENDING
| Copressor Sump Oil Change out as previously agreed upon |  |  |  |  | PENDING
C-1231F | N2 purge @ 10 psi |  |  |  |  | OK
| Interconnecting Piping - re-install |  |  |  |  | NOT STARTED
| Fiber-optic connections |  |  |  |  | COMPLETE
| 480 VT power - Transformer connection correction |  |  |  |  | PENDING
| Transmitter(s) - Re-install |  |  |  |  | PENDING
| Copressor Sump Oil Change out as previously agreed upon |  |  |  |  | PENDING
COMMENTS/OTHER:
| All previous alignment records will be reviewed against parameters. |  |  |  |  | PENDING
SERVICE TECHS TO DAILY LIST ALL MATERIAL SHORTAGES AND ANY
MATERIALS BORROWED FROM OTHER EQUIPMENT FOR USE NOW:
| XV-1231-A-4: Defective position transmitter - JCI-WABO to acquire. |  |  |  |  | PENDING
Reviewed Hot gas piping on "D" unit - Will confirm Items with JCI-WABO
| 1/Check valves missing - 2 are wrong size. - JCI discussing with Howard Fishman |  |  |  |  | PENDING