FV-1231A1 
29410052P32 659D2149(1) C4 

VALVE, CONTROL; 8" X 6" 150# RF; FISHER; MODEL
NUMBER: 585C-EWT; WCC STEEL; WHISPERFLO, X
LEVEL, NOISE ATTENUATING CAGE, TRIM # 901, 410
SST PLUG AND CAGE, 416 SST SEAT RING, NITRILE
BACK UP RING, 5.375" PORT, ANSI CLASS IV LEAKAGE
RATE, DOUBLE PTFE PACKING FOR
PRESSURE/VACUUM SERVICE. THE ACTUATOR IS A
SIZE 60 PISTON STYLE, 60 PSIG MINIMUM AIR SUPPLY,
5" TRAVEL, AIR TO CLOSE/FAIL OPEN ACTION
ACHIEVED BY USING A TYPE 377U TRIP VALVE AND
VOLUME TANK. THE I/P POSITIONER IS TYPE DVC6020,
AND THE STEM POSITION FEEDBACK TRANSMITTER
WILL BE THE TYPE 4221, 67CFR AIRSET, ALSO
INCLUDED WILL BE A REXROTH QUICK RELEASE VALVE
FOR FAST OPENING; WITH BYPASS AND NEEDLE
VALVE, STAINLESS STEEL TUBING AND SWAGELOK
FITTINGS. LSO INCLUDED WILL BE AN ASCO
EV8316G384VMB LOW POWERED SOLENOID VALVE, 24
VDC, HIGH TEMPERATURE COIL, CONTINUOUS DUTY,
IN 316 SST, CASING MOUNTED TO THE ACTUATOR
WITH STAINLESS STEEL TUBING AND SWAGELOK
FITTINGS
PER ATTACHED QUOTE (DJR022609 REV 2) ITEM 4
VENDOR NOT TO TAG

XV-1231A4 
29410052P39 659D2149(1) 

C4 VALVE, AUTO ISOLATION; 1" 150# RF; SHARPE; MODEL
NUMBER: SERIES 50; CS; ASTM A216 WCB BODY, 316 SS
BALL AND STEM, REINFORCED TEFLON SEAT, TEFLON
SEAL, FULL BORE, PNEUMATIC RACK AND PINION
ACTUATOR, SPRING RETURN, FAIL CLOSED, EPIC 360
SERIES D460 NON-CONTACT HART ENABLED POSITION
TRANSMITTER, 24VDC SS 3-WAY AIR DUMP SOLENOID,
CLASS 1 DIV II, GROUP C&D, 316 TUBING AND
FITTINGS. INCLUDE COST FOR BELLOFRAM AIR FILTER
REGULATOR.