# PART 1 - GENERAL                                                                                                 FORM 150.72-GS1

  - GENERAL REQUIREMENTS

The requirements of this Section shall conform to the general provisions of the Contract, including General and Supplementary Conditions, Conditions of the Contract, and Contract Drawings.

1.02 SCOPE

Provide Microprocessor controlled, twin-screw compressor, water-cooled, liquid chillers of the scheduled capacities as shown and indicated on the Drawings, including but not limited to:

- Chiller package with zero Ozone Depletion Potential Refrigerant R-410A

- Charge of refrigerant and oil

- Electrical power and control connections

- Chilled liquid connections

- Condenser liquid connections

- Manufacturer start-up

1.03 QUALITY ASSURANCE

- Products shall be Designed, Tested, Rated and Certified in accordance with, and Installed in compliance with applicable sections of the following Standards and Codes:

- AHRI 550/590 – Water Chilling Packages Using the Vapor Compression Cycle

- AHRI  575 – Method of Measuring Machinery Sound Within an Equipment Space

- ANSI/ASHRAE 15 – Safety Code for Mechanical Refrigeration

- ANSI/ASHRAE 34 – Number Designation and Safety Classification of Refrigerants

- ASHRAE 90.1 – Energy Standard for Buildings Except Low-Rise Residential Buildings

- ANSI/NFPA 70 – National Electrical Code (N.E.C.)

- ASME Boiler and Pressure Vessel Code, Section VIII, Division 1

- OSHA – Occupational Safety and Health Act

- Manufactured in facility registered to ISO 9001

- Conform to Intertek Testing Services for construction of chillers and provide ETL/cETL Listed Mark

- Factory Run Test: Chiller shall be pressure-tested, evacuated and fully charged with refrigerant and oil, and shall be factory operational run tested with water flowing through the vessel.

- Chiller manufacturer shall have a factory trained and supported service organization.

- Warranty: Manufacturer shall Warrant all equipment and material of its manufacture against defects in workmanship and material for a period of eighteen (18) months from date of shipment or twelve (12) months from date of start-up, whichever occurs first.

1.04 DELIVERY AND HANDLING

- Unit shall be delivered to job site fully assembled with all interconnecting refrigerant piping and internal wiring ready for field installation and charged with refrigerant and oil by the Manufacturer.

- Provide protective covering over vulnerable components for unit protection during shipment. Fit nozzles and open ends with plastic enclosures.

- Unit shall be stored and handled per Manufacturer’s instructions.

PART 2 - PRODUCTS

2.01 MANUFACTURERS

- The design shown on the Drawings is based on YORK model YLAA chiller manufactured by Johnson Controls / YORK. Alternate equipment will be acceptable if the manufacturer’s equipment meets the scheduled performance and complies with these specifications. If equipment manufactured by a manufacturer other than that scheduled is utilized, then the Mechanical Contractor shall be responsible for coordinating with the General Contractor and all affected Subcontractors to insure proper provisions for installation of the furnished unit. This coordination shall include, but not be limited to, the following:

- Structural supports for units.

- Piping size and connection/header locations.

- Electrical power requirements and wire/conduit and overcurrent protection sizes.

- Chiller physical size on plant layout.

- Site noise considerations.

- The Mechanical Contractor shall be responsible for all costs incurred by the General Contractor, Subcontractors, and Consultants to modify the building provisions to accept the furnished alternate equipment.

2.02 GENERAL

- Description: Furnish, Install, and Commission factory assembled, charged, and operational run tested air-cooled scroll compressor chiller as specified herein and shown on the Drawings. Chiller shall be designed, selected, and constructed using a refrigerant with Flammability rating of “1”, as defined by ANSI/ASHRAE STANDARD 34 Number Designation and Safety Classification of Refrigerants. Chiller shall include not less than two refrigerant circuits above 50 tons (200kW), scroll compressors, direct-expansion type evaporator, air-cooled condenser, refrigerant, lubrication system, interconnecting wiring, safety and operating controls including capacity controller, control center, motor starting components, and special features as specified herein or required for safe, automatic operation.

- Operating Characteristics: Provide low and high ambient temperature control options as required to ensure unit is capable of operation from 30°F to 115°F (-1°C to 46°C) ambient temperature.

[OPTIONAL]:  0°F to 125°F (-18°C to 52°C) ambient.]

- Cabinet: External structural members shall be constructed of heavy gauge, galvanized steel coated with baked on powder paint which, when subject to ASTM B117, 1000 hour, 5% salt spray test, yields minimum ASTM 1654 rating of “6”.

- Service Isolation valves:  Discharge (ball type) isolation valves factory installed per refrigerant circuit. Includes a system high-pressure relief valve in compliance with ASHRAE15.

- Pressure Transducers and Readout Capability

- Discharge Pressure Transducers: Permits unit to sense and display discharge pressure.

- Suction Pressure Transducers: Permits unit to sense and display suction pressure.

- High Ambient Control: Allows units to operate when the ambient temperature is above 115°F (46°C). Includes discharge pressure transducers.

- Shipping: Unit shall ship in one piece and shall require installer to provide only a single evaporator inlet and outlet pipe connection. If providing chiller model that ships in multiple pieces, bid shall include all the material and field labor costs for factory authorized personnel to install a trim kit to connect the pieces as well as all interconnecting piping and wiring.

2.03 COMPRESSORS

- Compressors: Shall be hermetic, scroll-type, including.

- Compliant design for axial and radial sealing.

- Refrigerant flow through the compressor with 100% suction cooled motor.

- Large suction side free volume and oil sump to provide liquid handling capability.

- Compressor crankcase heaters to provide extra liquid migration protection.

- Annular discharge check valve and reverse vent assembly to provide low-pressure drop, silent shutdown and reverse rotation protection.

- Initial oil charge.

- Oil level sight glass.

- Vibration isolator mounts for compressors.

- Brazed-type connections for fully hermetic refrigerant circuits.

- Compressor Motor overloads capable of monitoring compressor motor current. Provides extra protection against compressor reverse rotation, phase-loss and phase-imbalance.

2.04 REFRIGERANT CIRCUIT COMPONENTS

- Each refrigerant circuit shall include: a discharge service ball type isolation valve, high side pressure relief, liquid line shutoff valve with charging port, low side pressure relief device, filter-drier, solenoid valve, sight glass with moisture indicator, thermostatic expansion valves. [OPTIONAL]: electronic expansion valves

[OPTIONAL]: flexible, closed-cell foam insulated suction line

[OPTIONAL]: suction pressure transducer

2.05 HEAT EXCHANGERS

A. Evaporator:

- Evaporator shall be brazed-plate stainless steel construction capable of refrigerant working pressure of 650 psig (3103 kPa) and liquid side pressure of 150 psig (1034 kPa) (Option for 300 psig [2068 kPa] available).Constructed, tested, and stamped in accordance with applicable sections of ASME (PED) (GB) pressure vessel code for minimum 235 psig (16 barg) refrigerant side design working pressure and 150 psig (10 barg) liquid side design working pressure.

- Brazed plate heat exchangers shall be UL listed.

- Exterior surfaces shall be covered with 3.4” (19mm), flexible, closed cell insulation, thermal conductivity of 0.26k ([BTU/ HR-Ft2 -°F]/in.) maximum.

- Water nozzles shall be provided with grooves for field provided ANSI/AWWA C-606 mechanical couplings.

- Evaporator shall include vent and drain fittings and thermostatically controlled heaters to protect to -20°F (-29°C) ambient in off-cycle.

- A 20-mesh, serviceable wye-strainer and mechanical couplings shall be provided for field installation on evaporator inlet prior to startup.

- [OPTIONAL]: Evaporator shall be provided with piping extension kit and mechanical couplings to extend liquid connection from evaporator to edge of unit.  Thermal dispersion type flow switch shall be factory installed in the evaporator outlet pipe extension and wired to the unit control panel.  Insulation and heat trace on piping shall be responsibility of installing contractor.  Extension kit nozzle connections shall be ANSI/AWWA C-606 (grooved).

B. Air-Cooled Condenser:

- Coils: Condenser coils shall be constructed of a single material to avoid galvanic corrosion due to dissimilar metals. Coils and headers are brazed as one piece. Integral sub cooling is included. Coils shall be designed for a design working pressure of 650 PSIG (45 bar). Condenser coil shall be washable with potable water under 100 psi (7 bar) pressure.

- Low Sound Fans: Shall be dynamically and statically balanced, direct drive, corrosion resistant glass fiber reinforced composite blades molded into a low noise, full-airfoil cross section, providing vertical air discharge and low sound. Each fan shall be provided in an individual compartment to prevent crossflow during fan cycling. Guards of heavy gauge, PVC (poly- vinylchloride) coated or galvanized steel shall be factory installed.

- Fan Motors: High efficiency, direct drive, 6 pole, 3 phase, insulation class “F”, current protected, Totally Enclosed Air-Over (TEAO), rigid mounted, with double sealed, permanently lubricated, ball bearings.

2.06 POWER AND ELECTRICAL REQUIREMENTS

- Power/Control Panel:

- NEMA 3R/12 rain/dust tight, powder painted steel cabinets with hinged, latched, and gasket sealed outer doors. Provide main power connection(s), control power connections, compressor and fan motor start contactors, current overloads, and factory wiring.

- Power supply shall enter unit at a single location, be 3 phase of scheduled voltage, and connect to individual terminal blocks per compressor. Separate disconnecting means and/or external branch circuit protection (by Contractor) required per applicable local or national codes.

- Compressor, control and fan motor power wiring shall be located in an enclosed panel or routed through liquid tight conduit.

2.07 CONTROLS

- General: Automatic start, stop, operating, and protection sequences across the range of scheduled conditions and transients.

- Power/Control Enclosure: Rain and dust tight NEMA 3R powder painted steel cabinet with hinged, latched, and gasket sealed door.

- Microprocessor Control Center:

- Automatic control of compressor start/stop, anti-coincidence and anti-recycle timers, automatic pumpdown at system shutdown, condenser fans, evaporator pump, evaporator heater, unit alarm contacts, and chiller operation from 0°F to 125°F (-18°C to 52°C) ambient. Automatic reset to normal chiller operation after power failure.

- Remote water temperature reset via 0-10 VDC or 4-20 mA input signal or up to two steps of demand (load) limiting.

- Software stored in non-volatile memory, with programmed setpoints retained in lithium battery backed real-time-clock (RTC) memory for minimum 5 years.

- Forty character liquid crystal display, descriptions in English (or Spanish, French, Italian, or German), numeric data in English (or Metric) units. Sealed keypad with sections for Setpoints, Display/Print, Entry, Unit Options & clock, and On/Off Switch.

- Programmable Setpoints (within Manufacturer limits): display language; chilled liquid temperature setpoint and range, remote reset temperature range, daily schedule/holiday for start/stop, manual override for servicing, low and high ambient cutouts, low liquid temperature cutout, low suction pressure cutout, high discharge pressure cutout, anti-recycle timer (compressor start cycle time), and anti-coincident timer (delay compressor starts).

- Display Data: Return and leaving liquid temperatures, low leaving liquid temperature cutout setting, low ambient temperature cutout setting, outdoor air temperature, English or metric data, suction pressure cutout setting, each system suction pressure, discharge pressure (optional), liquid temperature reset via a 4-20milliamp or 0-10 VDC input, anti-recycle timer status for each compressor, anti-coincident system start timer condition, compressor run status, no cooling load condition, day, date and time, daily start/stop times, holiday status, automatic or manual system lead/lag control, lead system definition, compressor starts/operating hours (each), status of hot gas valves, evaporator heater and fan operation, run permissive status, number of compressors running, liquid solenoid valve status, load & unload timer status, water pump status.

- System Safeties: Shall cause individual compressor systems to perform auto shut down; manual reset required after the third trip in 90 minutes. System Safeties include: high discharge pressure, low suction pressure, high pressure switch, and motor protector. Compressor motor protector shall protect against damage due to high input current or thermal overload of windings.

- Safeties: Shall be automatic reset and cause compressors to shut down if low ambient, low leaving chilled liquid temperature, under voltage, and flow switch operation.

- Alarm Contacts: Low ambient, low leaving chilled liquid temperature, low voltage, low battery, and (per compressor circuit): high discharge pressure, and low suction pressure.

- BAS Communications:  YORKTalk 2, BACnet MS/TP, Modbus and N2 communication capabilities are standard.  (Option:  LON communication via ELink Microgateway).

- Manufacturer shall provide any controls not listed above, necessary for automatic chiller operation. Mechanical Contractor shall provide field control wiring necessary to interface sensors to the chiller control system.

2.10 ACCESSORIES AND OPTIONS

Some accessories and options supersede standard product features. All options are factory-mounted unless otherwise noted.

- Microprocessor controlled, Factory installed Across-the-Line type compressor motor starters as standard.

- Outdoor Ambient Temperature Control

- Low Ambient Control: Permits unit operation to 0°F ambient. Standard unit controls to 30°F ambient.

- High Ambient Control: Permits unit operation above 115°F ambient

- Power Supply Connections:

- Single Point Power Supply: Single point Terminal Block for field connection and interconnecting wiring to the compressors. Separate external protection must be supplied, by others, in the incoming power wiring, which must comply with the National Electric Code and/or local codes.

- Single Point or Multiple Point Disconnect: Single or Dual point Non-Fused Disconnect(s) and lockable external handle (in compliance with Article 440-14 of N.E.C.) can be supplied to isolate the unit power voltage for servicing. Separate external fusing must be supplied, by others, in the incoming power wiring, which must comply with the National Electric Code and/or local codes.

- Single Point Circuit Breaker: Single point Terminal Block with Circuit Breaker and lockable external handle (in compliance with Article 440-14 of N.E.C.) can be supplied to isolate power voltage for servicing. Incoming power wiring must comply with the National Electric Code and/or local codes.

- Control Power Transformer: Converts unit power voltage to 120-1-60 (500 VA capacity). Factory-mounting includes primary and secondary wiring between the transformer and the control panel.

- Power Factor Correction Capacitors: Provided to correct unit compressor factors to a 0.90-0.95.

- Condenser Coil Environmental Protection:

- Post-Coated Dipped: Dipped-cured coating on condenser coils for seashore and other corrosive applications (with the exception of strong alkalis, oxidizers, and wet bromine, chlorine and fluorine in concentrations greater than 100 ppm).

- Protective Chiller Panels (Factory or Field Mounted)

- Louvered Panels (condenser coils only): Painted steel as per remainder of unit cabinet, over external condenser coil faces.

- Wire Panels (full unit): Heavy gauge, welded wire- mesh, coated to resist corrosion, to protect con- denser coils from incidental damage and restrict unauthorized access to internal components.

- Louvered Panels (full unit): Painted steel as per re- mainder of unit cabinet, to protect condenser coils from incidental damage, visually screen internal components, and prevent unauthorized access to internal components.

- Louvered/Wire Panels: Louvered steel panels on external condenser coils painted as per remainder of unit cabinet. Heavy gauge, welded wire-mesh, coated to resist corrosion, around base of machine to restrict unauthorized access.

- End Louver (hail huard): Louvered steel panels on external condenser coil faces located at the ends of the chiller.

- Thermal Dispersion Flow Switch (Factory installed and wired in piping extension kit):  Normally open, 30bar pressure rating, stainless steel 316L construction, IP67, -4°F to 158°F ambient rating.

- Evaporator options: Provide 1-1/2”” evaporator insulation in lieu of standard 3/4”.

- Hot Gas By-Pass: Permits continuous, stable operation at capacities below the minimum step of unloading to as low as 5% capacity (depending on both the unit & operating conditions) by introducing an artificial load on the evaporator. Hot gas by-pass is installed on only one refrigerant circuit.

- Low Temperature Process Glycol: Leaving chilled liquid setpoint range 10°F to 50°F (-12°C to 10°C.

- Chicago Code Relief Valves to meet Chicago Code requirements.

- Sound Reduction (Factory installed):

- Ultra Quiet - Low speed, reduced noise fans.

- Compressor Acoustic Sound Blankets.

- Vibration Isolation (Field installed):

- Elastomeric Isolators.

- 1” Deflection Spring Isolators: Level adjustable, spring and cage type isolators for mounting under the unit base rails.

- 2” Deflection Restrained Spring Isolators: Level adjustable, restrained mounts in rugged welded steel housing with vertical and horizontal limit stops. Housings shall be designed to withstand a minimum 1.0g accelerated force in all directions to 2 inches (50.8 mm).

PART 3 - EXECUTION

3.01 INSTALLATION

- General: Rig and Install in full accordance with Manufacturer’s requirements, Project drawings, and Contract documents.

- Location: Locate chiller as indicated on drawings, including cleaning and service maintenance clearance per Manufacturer instructions. Adjust and level chiller on support structure.

- Components: Installing Contractor shall provide and install all auxiliary devices and accessories for fully operational chiller.

- Electrical: Coordinate electrical requirements and connections for all power feeds with Electrical Contractor (Division 16).

- Controls: Coordinate all control requirements and connections with Controls Contractor.

- Finish: Installing Contractor shall paint damaged and abraded factory finish with touch-up paint matching factory finish.