## Slide 1: YLAA Air Cooled Scroll Chiller Refresh Overview 50 – 150 Tons 175 – 540 kW
Finding the right balance for improved performance
Latin America Update
July 20, 2012

## Slide 2: Agenda
  Presenter introductions
  YLAA product and market review
  “Refresh project” overview & technical details
  YORKworks “Global Chiller Selection Software” demonstration
  New Sales Tools:
    Customer presentation, Sales Guide, Engineering guide
  Questions

## Slide 3
YLAA & Market Review

## Slide 4: YLAA Overview A brief history…
  Replaced R-22 chillers with R-410A, market leading performance
  Led the market globally for 3 years – hospitals, education, light commercial top segments
  Enabled significant growth in Latin America
  Multi-tier strategy proven successful
        SE benefits footprint, low first cost, performance
        HE offers a high efficiency value proposition
2007…YLAA launched
  Successful Options:
    Efficiency tiers
    Multiple sound levels
    Scalable option strategy
    Integrated pump kits
  Sales Trends:
    Globally: 60% SE, 40% HE
    LA: 75% SE in 2011
    NA: 65% SE
    Europe: 75% HE
    Asia: only offers HE

## Slide 5: YLAA Overview Industry Trends
Industry Trends, past and future:
  Green buildings and energy costs… …raise efficiency, reduce sound & refrigerant charge quantity
  Brazed Plate Evaporators, Microchannel… …technologies improve, reduce charge
  Pump kits… …add application range, options
  Fan sound levels… …improve industry-wide
  VSD fans… …improve part load efficiency
Summary:
  New technologies offer opportunity for improvement
  No major competitive changes expected until next round of efficiency legislation (2015)

## Slide 6: YLAA Overview Competitive Landscape
  Globally:
    Competitors offer wider range of applications
    New Trane CGAM performance higher, but with larger footprint
    Some new European competitors have good part load and footprint, but lack application range
    Carrier lags market and due for a product refresh
  Latin America:
    YLAA “SE” full load efficiency lags market
      was tightly optimized for footprint at launch
    HE full load lags Trane 3 – 4% (CGAM larger footprint units)
    Pump kits lack specifiable options

## Slide 7: YLAA Overview Competitive Landscape (Current YLAA)
A challenging segment, also local manufacturers

## Slide 8: YLAA – YORK Air-Cooled Scroll Chiller Competitive benchmarking – Where we are today
 | YLAA | CGAM | 30RB
(heat recovery, low ambient, high ambient) |  |  | 
Trane CGAM good performance but large footprint & charge.
Carrier 30RB lags market and due for design refresh.
Above Average
Average
Below Average

## Slide 9: YLAA Overview Competitive Landscape…where we are today
YLAA still a good balance of efficiency, sound, charge and footprint, but competitors have closed the gap

## Slide 10
YLAA Refresh Project

## Slide 11: Refresh Project What, Why, How?
  We have talked about where we are today, the market, and the competition
  We must continue to develop to remain competitive
  A product line refresh was mapped out with several steps:
    New Options – industry leading glycol and heat recovery options
      Controls and technology to operate better
      Structure as options – only pay for it when it’s needed
    Brazed Plate Evaporators less weight, less volatility to Copper, price reduction
      Combined with microchannel for a low refrigerant charge
    New 50Hz SE models with higher efficiency, 50Hz HE range extension to 550kW
    New VSD fan option for HE part load improvement
    New Pump options and range
    New Premium Efficiency with low footprint
A large investment, including focus on 50Hz gaps.
Technical hurdles passed, drafting and implementation in progress.

## Slide 12
YLAA Schedule

## Slide 13: Refresh Project Schedule
  New Options: Glycol & Heat Recovery
    Launched August 2011
  New Brazed Plate Models
    First stage (4, 5, 6 fan) in YORKworks now
    Remaining units available in October
  New 50Hz SE models
    Early 2013 (calendar year)
  VSD Fan Option
    SQ today, early 2013 option
  Pumps
    Staged with new BPHX models
    VSD pump design pending, can SQ today
  Premium Efficiency
    2013 development
    2014 release
  New Sales Tools!
    New Sales Guide
    New Customer Presentation
    New Engineering Guides

## Slide 14
YLAA Sales Tools

## Slide 15: YORKworks GCSS Global Integration
  GCSS is the global selection tool, transitioning products during 2012
  More consistent documentation, ratings, reports, implementation timing
  Demonstration of new options, features during demonstration later

## Slide 16: Sales Tools
Sales Guide
Form: PUBL-6886
60Hz Engineering Guide
Form: 150.72-EG6
50Hz Engineering Guide
Form: 150.72-EG8
Customer Presentation
Available on portal (review later)

## Slide 17: Information Access
Internal Portal
Products & Services >
Products > North America > Chillers
External Website
BPHX will be added in a few days

## Slide 18
YLAA Technical Details

## Slide 19: Points to remember
  Five important items to remember:
  Our glycol chiller can stay loaded at higher ambient
  Heat Recovery makes more usable heat, offers flexible performance range
  Brazed plate reduces weight, has price advantage
  VSD fan option on HE to improve part load, where chillers operate 97% of the time
  Two levels of pump kits, match to customer needs

## Slide 20: Refresh Project Overview 1. Glycol and Heat Recovery (Options)
  Glycol Chilling Option: 10F (-12C) low limit
    YLAA keeps making more capacity at higher ambients due to intelligent control
  Heat Recovery Condenser Option: “Partially Condensing”
    up to 85% heat recovered – much more usable heat than desuperheater (10%)
    temperature to 60C (up to 20% HR at this condition)
    global design leverages volume
  Differentiators:
    Glycol lower than all but Trane CGAM (matches); YLAA stays loaded intelligently
    Partially condensing heat recovery makes more usable heat

## Slide 21: Technical Details 1. Glycol – maximum capacity, colder glycol at higher ambient
  Low temperature needs smaller expansion valve
    YLAA glycol option uses Electronic Expansion Valve (EEV)
    EEV also facilitates changeover duty with no derate at comfort cooling
  At low temperatures, compressor envelopes are small
    YLAA engineers designed an unload feature to keep the chiller making as much capacity as possible, even when ambient is high
Suction Temperature
Condenser Temperature
Maximum capacity & colder glycol at higher ambient
No capacity penalty in changeover applications

## Slide 22: Technical Details 1. Heat Recovery – more heat, more flexibility
  “Partially Condensing Heat Recovery”
  Best balance of total heat recovered, temperature, and cost
  Flexibility to dial performance to customer needs
  YLAA design a global standard, shared components keeps cost competitive
Recovery Type | What is it? | HR Capacity | HR Temp. | Notes
Partially Condensing | Medium BPHX in discharge line | up to 85% | High (60C), Medium (40-50C) | YLAA design Excellent balance of performance, flexibility and price
Desuperheater | Small BPHX in discharge line | up to 10% | High (60C) | Used by Trane, Carrier and others
Secondary Condenser | Water-cooled condenser in parallel with air-cooled | 100% (no less) | Low (35-40C) | Unique to Carrier High price Refrigerant system complexities
Partially condensing heat recovery offers wide range of capacity and temperatures, at competitive cost

## Slide 23: Technical Details 1. Heat Recovery – more heat, more flexibility
  Amount of heat recovered depends on leaving hot water temperature
  Recovery potential is cooling load plus work input
    some competitors choose to ignore work input – to show higher heat recovery percentage
  Heat recovery increases chiller efficiency slightly (depending on air temperature)
THR is what matters to our customers

## Slide 24: Refresh Project Overview 2. Brazed Plate Evaporators (4-6 fan available now, 8-10 fan 2013)
  A weight savings of 10-15%
  Less structural steel, crane costs required on site
  Reduced copper use – price reduction
  Shell & tube still available today; phase out plan to be determined in next few weeks

## Slide 25: Technical Details 2. Brazed Plate Evaporator (4-6 fan available now, 8-10 fan 2013)
  Why Now?
  Performance lacking 5 years ago
    copper costs driving development
    technology now competitive to 700 kW
    No performance impact
Changes Required:
  Testing, testing, testing….
    Multiple sizes, full and part load, extreme conditions
    Performance meets or exceeds shell & tube
  Drafting
    Unique opportunity to incorporate best practices
    New pump kits, piping, sheet metal
  Shell & tube still available today; phase out plan to be determined in next few weeks

## Slide 26: Technical Details 2. Brazed Plate Evaporator (4-6 fan available now, 8-10 fan 2013)
  New evaporator:
  316 stainless steel plates optimized for HFC-410A
  20-mesh wye-strainer included standard
    Risk of clogging primarily construction debris at startup (evap loop is closed)
    Strainer can be serviced or mesh removed after startup
    Pump kits have strainers already (and will continue)

## Slide 27: Technical Details 2. Brazed Plate Evaporator (4-6 fan available now, 8-10 fan 2013)
  Customer connections to brazed plate evaporator:
  4 - 6 fan: end connection (shown below); 8 - 10 fan: right side connection (not shown)
  Evaporator back from edge to help Center of Gravity, minimize refrigerant piping
  Standard “extension kit” – moves water connection to edge of unit, includes flow switch
Right Side View – Heat Recovery
End View – Evaporator & pump kit
Control Panel
Control Panel

## Slide 28: Refresh Overview 3. New 50Hz SE & HE models (2013 release)
50Hz SE goals:
    Improve part load efficiency to 2.70 COP
    Remain comparable to major competitors
    Offer base efficiency at best footprint, value
  Achieved with combination of evaporator and condenser changes
50Hz HE goals:
    Overlap YVAA and have a tiered offering at this key design shift point
    YVAA starts at 500 kW
  Achieved by adding a new 10-fan model, capacity 550 kW
New models will be available with BPHX only

## Slide 29: Technical Details 3. New 50Hz SE Models (2013 release)
Model (old/new) | Current Cap. (kW) | Curr.COP | New Cap. | New COP | Changes | Footprint Change?
180SE | 179 | 2.84 | 188 | 2.96 | Cooler Size | No
210SE 211SE | 196 | 2.41 | 202 | 2.75 | Compressors +1 Fan & Coil | Yes
240SE | 218 | 2.69 | 223 | 2.71 | Cooler Size | No
320SE 321SE | 310 | 2.56 | 326 | 2.84 | +2 Fans & Coils | Yes
360SE 361SE | 344 | 2.66 | 353 | 2.80 | +1 Fan & Coil | Yes
400SE 401SE | 386 | 2.55 | 401 | 2.70 | +1 Fan & Coil | Yes
485SE 486SE | 466 | 2.57 | 485 | 2.78 | +2 Fans & Coils | Yes
New HE model is a 10-fan unit, similar footprint to YVAA

## Slide 30: Competitive Comparison 3. New 50Hz Models – Full Load and Footprint (2013 release)
Competitive full load efficiency
Leading footprint in most sizes

## Slide 31: Refresh Overview 4. VSD Fans (New HE Option) (SQ now, 2013 option)
VSD Fans
  New option on HE units
  Improves sound, efficiency – entire coil active
  Design similar to YVAA
    Add-on inverter enclosure with fan terminals
    Allows future retrofit kit for of installed units
Unit
Panel
Metal Wiring tray
VSD
One inverter per system

## Slide 32: Performance Overview 4. VSD Fan Option – Part Load Efficiency (SQ now, 2013 option)
  Gains 3-8% depending on unit size and configuration
  Graphed with competition:
Conservative estimates…testing ongoing!
2014 “PE” project target

## Slide 33: Refresh Overview 5. Pump Kit Improvements (available now, BPHX units)
  Wider range of selections to include:
    Primary-Secondary (down to 1.5 kW motors)
    More impeller sizes – better match job
  New Optional “Full Featured” Kit
    Test ports, drain ports, expansion tank port
    Base kit as today, plus drain/vent ports, flow switch
  VSD Pumps by SQ
    Future standard option

## Slide 34: Technical Details 5. Pumps Kits – wider range, new options (available now, BPHX units)
IGV = inlet guide vane / strainer
  YLAA was a leader in factory-installed pump kits
  Our competitors have evolved and expanded
    Trane standardized CGAM on VFDs for balancing & setup
    Carrier offers tanks, optional VFDs
    Both offer service valves
 | Dual Pump | VFD | IGV | Comb. Valve | PT Taps | Service Valves | Expansion Tank
Trane CGAM |  |  |  |  |  |  | 
Carrier 30RB |  |  |  |  |  |  | 
York YLAA |  |  |  |  |  |  | 
The new pump kits address all of these items
(SQ)

## Slide 35: Technical Details 5. Pumps Kits – wider range, new options (available now, BPHX units)
  Two levels of pump kits:
    Base as today, plus shutoff valves (IGV, flow switch, balancing valve, pump, shutoff valves)
    Full featured with above plus test ports, drains
    VSDs and expansion tanks by SQ (future options)
  Also offering a wider range of pumps
    smaller motors suitable for primary-secondary;
    more impeller sizes for better efficiency match to duty
  New rating software into GCSS…flexibility, reports
  Balancing valve a good idea…even with VFD!
    recommended by pump manufacturers; allows fine tuning flow
    Includes check valve function, shutoff valve and drain – fewer connections
    a differentiator for YLAA
Increased flexibility, performance and easier to do SQ’s…

## Slide 36: Technical Details 5. Pumps Kits – wider range, new options (available now, BPHX units)
Similar to current pump kit, with:
New vent & drain port in piping, flow switch

## Slide 37: Technical Details 5. Pumps Kits – wider range, new options (available now, BPHX units)
Same as standard kit, plus inlet shutoff valve, additional ports for expansion tank and pressure/temperature measurement

## Slide 38: Technical Details 5. Pumps Kits – wider range, new options (available now, BPHX units)

## Slide 39: Summary and Questions
  Remember:
  Our glycol chiller can stay loaded at higher ambient
  Heat Recovery makes more usable heat, offers customizable performance
  Brazed plate reduces weight, has price advantage
  VSD fan an option on HE to improve part load, where chillers operate 97% of the time
  Two levels of pump kits, match to customer needs
YLAA offers an excellent balance… Performance, flexibility, footprint, sound, and price
New features expand this position – sell the value
Bring us opportunities to help you win!

## Slide 40
Appendix
  Competitive Note
  Heat Recovery Piping
  GCSS Screenshots

## Slide 41: Competitive Note Carrier Heat Recovery
Carrier Heat Recovery condenser is a Desuperheater type.
There are a few disadvantages to the design:
    Low percentage of heat recovered (up to 10% THR)
    A single brazed plate evaporator in each circuit. This makes field piping much more complex.
    Condensers are not insulated for efficiency, or heat traced for winter storage. Adds field install labor and complexity.
YLAA uses a Partially Condensing heat recovery condenser. This design allows maximum flexibility to the user for heat and temperature balance, up to 85% THR and 60C (at lower %’s).
The YLAA also uses a single (dual circuit) condenser, for easier field piping install. And it is heat traced, with power from the unit panel. Insulation is standard.
Specify a single heat recovery condenser, heat trace and insulation.
Help design systems with high % heat recovery.
Explain the extra costs to contractors.

## Slide 42: Heat Recovery Piping Recommendation
Closed loop should be used for heating potable water, pools

## Slide 43: Global Chiller Selection Software Screenshot overview
New entry on drop-down menu
Old:
Small Tonnage Chiller Products
New:
Global Chiller Selection Software

## Slide 44: Global Chiller Selection Software Screenshot overview
Note:
Style A = Shell & Tube
Style B = BPHX
Step 1:
Make new project
Step 2:
Select unit types to rate
-or-
Select specific unit

## Slide 45: Global Chiller Selection Software Screenshot overview
Basic rating and selection screen
Step 3: Enter design conditions temperatures, voltage, liquid types
Step 4:
Click Rate

## Slide 46: Global Chiller Selection Software Screenshot overview
Rating Results
Step 5:
Review performance data and re-rate or re-select if necessary

## Slide 47: Global Chiller Selection Software Screenshot overview
Options and Reports
Step 6:
Select options, PCAT, access reports across top of screen