## Slide 1: YLAA Air Cooled Scroll Chiller Refresh Overview 60 – 175 Tons
Finding the right balance for improved performance
North America Update
August 13, 2012

## Slide 2: Presenter Introductions
  Nicholas Staub, Product Portfolio Manager - North America
  Christian Rudio, Global Product Line Manager - Scrolls
  David Wolf, Application Engineer - Screw and Scroll Products

## Slide 3: Today’s Expected Outcomes
Learn about our STC market potential, our share and ways to increase visibility
Learn about five new ways to promote and specify our YLAA offering with your consultants to:
        Expand margin on every sale
        Increase system performance and reliability
        Outsmart your competition by driving up their costs
Learn more about our Global Chiller Selection software, our latest improvements and best practices around optimizing chiller selections
Need a Subject Matter Expert or sales materials to help you WIN more YLAA projects? You will meet the JCI STC Team today...they will help!

## Slide 4: Agenda
  YLAA product and market review
  “Refresh project” overview & technical details
    Glycol Applications
    Heat Recovery
    Brazed Plate Heat Exchanger
    VSD Fan Option
    Pump Kits – 2 different levels
  YORKworks “Global Chiller Selection Software” demonstration
  New Sales Tools:
    Customer presentation, Sales Guide, Engineering guide
  Questions

## Slide 5
YLAA SHARE OF MARKET BY REGION
$2.4 Mil
$2.9 Mil
$6.7 Mil
$7.5 Mil
$2.0 Mil
$3.9 Mil
$4.6 Mil

## Slide 6
YLAA SHARE OF MARKET BY REGION
$30 Million

## Slide 7
YLAA Vertical Market Applications
Chart: YLAA - Sales by Vertical Market
| Public - Local - Schools (K-12) | Public - Federal - Military - Other | Private - Health Care | Public - State - Higher Education | Public - Local - Other (incl. Board, Court, Munic. Serv., Etc. | Private - Other Manufacturing | Private - Higher Education | Private - Commercial Real Estate | Private - Petrochemical and Chemical Industry | Private - Associations, Services, Software, Religious
 | 0.19194 | 0.074496 | 0.071867 | 0.067485 | 0.064855 | 0.06135 | 0.042068 | 0.028922 | 0.025416 | 0.022787
      Top 5 (50% orders): K-12, Healthcare, Hotel, Federal Military, Local “other”
      Opportunity on Manufacturing/Industrial, Real Estate/Financial Offices

## Slide 8
What is the BEST Way to Penetrate this Hidden YLAA Market?
  Review your Branch Market Plan with your BM/BAM
    Review ARI performance, assigned accounts and account mgmt strategies
  Seek opportunities through the following customers/ channels:
    Customers you already call on
    Design Build Contractors
    Service Contractors
    JCI Service team
    UPG Distributors
    Maintenance dept within K12, Higher Ed and CRE
    Local Rigging Contractors

## Slide 9
YLAA & Market Review

## Slide 10: YLAA Overview A brief history…
  Replaced R-22 chillers with R-410A, market leading performance
  Led the market globally for 3 years – hospitals, education, light commercial top segments
  Contributed to significant growth in North America
  Multi-tier strategy proven successful
        SE benefits footprint, low first cost, performance
        HE offers a high efficiency value proposition
2007…YLAA launched
  Successful Options:
    Efficiency tiers
    Multiple sound levels
    Scalable option strategy
    Integrated pump kits
  Sales Trends:
    Globally: 60% SE, 40% HE
    NA: 65% SE
    LA: 75% SE in 2011
    Europe: 75% HE
    Asia: only offers HE

## Slide 11: YLAA Overview Industry Trends
Industry Trends, past and future:
  Green buildings and energy costs… …raise efficiency, reduce sound & refrigerant charge quantity
  Brazed Plate Evaporators, Microchannel… …technologies improve, reduce charge
  Pump kits… …add application range, options
  Fan sound levels… …improve industry-wide
  VSD fans… …improve part load efficiency
Summary:
  New technologies offer opportunity for improvement
  No major competitive changes expected until next round of efficiency legislation (2015)

## Slide 12: YLAA Overview Competitive Landscape (Current YLAA)

## Slide 13: YLAA – YORK Air-Cooled Scroll Chiller Competitive benchmarking – Where we are today
Trane CGAM good performance but large footprint & charge.
Carrier 30RB lags market and due for design refresh.
Above Average
Average
Below Average

## Slide 14: YLAA Overview Competitive Landscape…where we are today
YLAA still a good balance of efficiency, sound, charge and footprint, but competitors have closed the gap
Very competitive part load performance, goal is to stay the market leader
Only manufacturer to offer two efficiency tiers, you can select your cost point

## Slide 15
YLAA Refresh Project

## Slide 16: Refresh Project What, Why, How?
  We talked about where we are today, the market, and the competition
  We must continue to develop to remain competitive
  A product line refresh was mapped out with several steps:
    New Options – industry leading glycol and heat recovery options
      Controls and technology to operate better
      Structure as options – only pay for it when it’s needed
    Brazed Plate Evaporators less weight, less volatility to copper
      Combined with microchannel for a low refrigerant charge
    New VSD fan option for HE part load improvement
    New Pump options and range
    New Premium Efficiency with low footprint
A large investment designed to maintain industry leadership.
Technical hurdles passed, drafting and implementation in progress.

## Slide 17
YLAA Schedule

## Slide 18: Refresh Project Schedule
  New Options: Glycol & Heat Recovery
    Launched August 2011
  New Brazed Plate Models
    First stage in YORKworks GCSS now (4, 5, 6 fan)
    Remaining units available in October
  VSD Fan Option
    Early 2013 option
  New Pump Kits
    Available on new BPHX models
    VSD pump design pending, can SQ today
  Premium Efficiency
    2013 development
    2014 release
  New Sales Tools!
    New Sales Guide
    New Customer Presentation
    New Engineering Guides

## Slide 19
YLAA Technical Details

## Slide 20: Points to remember
  Five important items to remember:
  Lowest leaving glycol temperatures
  Heat Recovery, gives more usable heat
  Brazed plate reduces weight, integrates flow switch and strainer for reliability
  VSD fan option on HE to improve part load
  Two levels of pump kits, match to customer needs

## Slide 21: Technical Details 1. Glycol – maximum capacity, colder glycol at higher ambient
  Glycol Chilling Option: 10F leaving temperature
    YLAA keeps making more capacity at higher ambients due to intelligent control
    EEV also facilitates changeover duty with no derate at comfort cooling
Maximum capacity & colder glycol at higher ambient
No capacity penalty in changeover applications

## Slide 22: Technical Details 2. Heat Recovery – more heat, more flexibility
  “Partially Condensing Heat Recovery”
  Best balance of total heat recovered, temperature, and cost
  Flexibility to dial performance to customer needs
  YLAA design a global standard, shared components keeps cost competitive
Recovery Type | What is it? | HR Capacity | HR Temp. | Notes
Partially Condensing | Medium BPHX in discharge line | up to 85% | High (140F), Medium (100-125F) | YLAA design Excellent balance of performance, flexibility and price
Desuperheater | Small BPHX in discharge line | up to 10% | High (140F) | Used by Trane, Carrier and others
Secondary Condenser | Water-cooled condenser in parallel with air-cooled | 100% (no less) | Low (95-105F) | Unique to Carrier High price Refrigerant system complexities
Partially condensing heat recovery offers wide range of capacity and temperatures, at competitive cost

## Slide 23: Refresh Project Overview 3. Brazed Plate Evaporators (4-6 fan available now, 8-10 fan 2013)
  Average weight savings of 15%
  Less structural steel, crane costs required on site
  Reduced copper use – reduces price volatility
  Shell & tube still available for existing jobs, new selections BPHX only

## Slide 24: Technical Details 3. Brazed Plate Evaporator (4-6 fan available now, 8-10 fan 2013)
  Why Now?
  Performance lacking 5 years ago
    copper costs driving development
    technology now competitive to 200TR
    No performance loss, lower water PD
Changes Required:
  Testing, testing, testing….
    Multiple sizes, full and part load, extreme conditions
    Performance meets or exceeds shell & tube
  Drafting
    Unique opportunity to incorporate best practices
    New pump kits, piping, sheet metal

## Slide 25: Technical Details 3. Brazed Plate Evaporator (4-6 fan available now, 8-10 fan 2013)
  New evaporator:
  316 stainless steel plates optimized for HFC-410A
  Thermal dispersion flow switch standard
  20-mesh wye-strainer included standard
    Risk of clogging primarily construction debris at startup (evap loop is closed)
    Strainer can be serviced or mesh removed after startup
    Pump kits have strainers already (and will continue)

## Slide 26: Technical Details 3. Brazed Plate Evaporator (4-6 fan available now, 8-10 fan 2013)
  Customer connections to brazed plate evaporator:
  4 - 6 fan: end connection (shown below); 8 - 10 fan: right side connection (not shown)
  Evaporator back from edge to help Center of Gravity, minimize refrigerant piping
  Standard “extension kit” – moves water connection to edge of unit, includes flow switch
Right Side View – Heat Recovery
End View – Evaporator & pump kit
Control Panel
Control Panel

## Slide 27
Technical Details 3. Brazed Plate Evaporator versus Shell and Tube
Clogging - The factory will include a 20 mesh strainer at no additional cost.
Smaller Evaporator - Enables new features and options
    Water pipe extensions, water piping to edge of the unit (standard)
    Thermal dispersion flow switch (standard)
    Larger pump selections, with VSD
    Lower unit weights
Competition - Trane and McQuay scroll chillers are designed with BPHX.

## Slide 28: Refresh Overview 4. VSD Fans (New HE Option) (Available early 2013)
VSD Fans
  New option on HE units
  Improves sound, efficiency – entire coil active
  Design similar to YVAA
    Add-on inverter enclosure with fan terminals
    Allows future retrofit kit for of installed units
Unit
Panel
Metal Wiring tray
VSD
One inverter per system

## Slide 29: Performance Overview 4. VSD Fan Option – Part Load Efficiency (Available early 2013)
  Gains 3-8% depending on unit size and configuration
  Graphed with competition:
Conservative estimates…testing ongoing!

## Slide 30: Refresh Overview 5. Pump Kit Improvements (available now, BPHX units)
  Wider range of selections to include:
    Primary-Secondary (down to 3hp motors)
    More impeller sizes – better match jobs
  New Optional “Full Featured” Kit
    Inlet shutoff valve, Test ports, drain ports, expansion tank port
    Base kit as today, plus drain/vent ports
  VSD Pumps by SQ
    Future standard option
Increased flexibility, performance and easier to do SQ’s…
  Balancing valve a good idea…even with VFD!
    recommended by pump manufacturers; allows fine tuning flow
    Includes check valve function, shutoff valve and drain – fewer connections - Included as standard!

## Slide 31: Technical Details 5. Pumps Kits – wider range, new options (available now, BPHX units)
IGV = inlet guide vane / strainer
  YLAA was a leader in factory-installed pump kits
  Our competitors have evolved and expanded
    Trane standardized CGAM on VFDs for balancing & setup
    Carrier offers tanks, optional VFDs
    Both offer inlet service valves
 | Dual Pump | VFD | IGV | Comb. Valve | PT Taps | Service Valves | Expansion Tank
Trane CGAM |  |  |  |  |  |  | 
Carrier 30RB |  |  |  |  |  |  | 
York YLAA |  |  |  |  |  |  | 
The new pump kits address all of these items
(SQ)

## Slide 32: Technical Details 5. Pumps Kits – wider range, new options (available now, BPHX units)
Similar to current pump kit, with:
New vent & drain port in piping, flow switch

## Slide 33: Technical Details 5. Pumps Kits – wider range, new options (available now, BPHX units)
Same as standard kit, plus inlet shutoff valve, additional ports for expansion tank and pressure/temperature measurement

## Slide 34: Technical Details 5. Pumps Kits – wider range, new options (available now, BPHX units)

## Slide 35
YLAA GCSS Demonstration

## Slide 36
Global Chiller Selection Software Improvements / Concerns
Improvements over old STC software:
  Access more information without having to save project
  Ability to return to unit pick list without re-rating all models
  Unit pick lists show BTP pricing
  Can compare option and warranty pricing without saving
  Ability to handle worldwide products and users with one software tool
  Ability to update software without a patch
Major Issues Identified:
  Efficiency, unit of measure (COP, EER, KW/ton)
  Can’t rate by a temperature and flow
  Can’t rate heat pumps easily (YVWA)
  Option availability
  Drawings in .dwg format
  Need more descriptive error messages
  Need option description / cutsheets added

## Slide 37: Global Chiller Selection Software Screenshot overview
New entry on drop-down menu
Old:
Small Tonnage Chiller Products
New:
Global Chiller Selection Software

## Slide 38: Global Chiller Selection Software Screenshot overview
Note:
Style A = Shell & Tube
Style B = BPHX
Step 1:
Make new project
Step 2:
Select unit types to rate
-or-
Select specific unit

## Slide 39: Global Chiller Selection Software Screenshot overview
Basic rating and selection screen
Step 3: Enter design conditions temperatures, voltage, liquid types
Step 4:
Click Rate

## Slide 40: Global Chiller Selection Software Screenshot overview
Rating Results
Step 5:
Review performance data and re-rate or re-select if necessary

## Slide 41: Global Chiller Selection Software Screenshot overview
Options and Reports
Step 6:
Select options, PCAT, and warranty across top of screen

## Slide 42: Global Chiller Selection Software Screenshot overview

## Slide 43
Step 7:
Select the reports that you need including AHRI Part load
Global Chiller Selection Software Screenshot overview

## Slide 44
YLAA Sales Tools

## Slide 45: Sales Tools
Sales Guide
Form: PUBL-6886
60Hz Engineering Guide
Form: 150.72-EG6
50Hz Engineering Guide
Form: 150.72-EG8
Customer Presentation
Available on portal (review later)

## Slide 46: Information Access
Internal Portal
Products & Services >
Products > North America > Chillers
External Website
BPHX will be added in a few days

## Slide 47: Summary and Questions
  Remember:
  Our glycol chiller can stay loaded at higher ambient
  Heat Recovery makes more usable heat, offers customizable performance
  Brazed plate reduces weight, integrates flow switch and strainer for reliability
  VSD fan an option on HE to improve part load, where chillers operate 97% of the time
  Two levels of pump kits, match to customer needs
YLAA offers an excellent balance… Performance, flexibility, footprint, sound, and price
New features expand this position – sell the value
Bring us opportunities to help you win!

## Slide 48
Appendix
  Competitive Note
  Heat Recovery Piping
  GCSS Screenshots

## Slide 49: Technical Details 1. Heat Recovery – more heat, more flexibility
  Amount of heat recovered depends on leaving hot water temperature
  Recovery potential is cooling load plus work input
    some competitors choose to ignore work input – to show higher heat recovery percentage
  Heat recovery increases chiller efficiency slightly (depending on air temperature)
THR is what matters to our customers

## Slide 50: Competitive Note Carrier Heat Recovery
Carrier Heat Recovery condenser is a Desuperheater type.
There are a few disadvantages to the design:
    Low percentage of heat recovered (up to 10% THR)
    A single brazed plate condenser in each circuit. This makes field piping much more complex.
    Condensers are not insulated for efficiency, or heat traced for winter storage. Adds field install labor and complexity.
YLAA uses a Partially Condensing heat recovery condenser. This design allows maximum flexibility to the user for heat and temperature balance, up to 85% THR and 60C (at lower %’s).
The YLAA also uses a single (dual circuit) condenser, for easier field piping install. And it is heat traced, with power from the unit panel. Insulation is standard.
Specify a single heat recovery condenser, heat trace and insulation.
Help design systems with high % heat recovery.
Explain the extra costs to contractors.

## Slide 51: Heat Recovery Piping Recommendation
Closed loop should be used for heating potable water, pools