## Slide 1: STC Air Cooled Chillers
YLAA – YCIV - YVAA
Nantes Sales Training November 2014 Roger Smeed

## Slide 2: YVAA – YORK Variable Speed Air-Cooled Screw Chillers Introducing model range’s
YLRA/YLPA - Scroll HP
180-640 kW
YVAA- VSD Screw Comp (2nd Gen.) 525-1660 kW
YCIV- VSD Screw Comp (1st Gen.) 540-1450 kW (Special applications. Only)
YLAA - Scroll Comp
180-520 kW
kW
0 200 400 600 800 1000 1200 1400 1600 1800
YLxA
40-150
kW

## Slide 3
YLAA Air-Cooled Scroll Chiller
3
Roger Smeed
Notes: 3

## Slide 4: Air Cooled Chillers, Industry Factors Effecting YLAA
  Green buildings and energy costs… …raise efficiency, reduce sound & refrigerant charge quantity
  Brazed Plate Evaporators, Microchannel… …technologies improve, reduce charge reduced unit weight,
  Pump kits for ease insulation… …add application range, options
  Reduced sound levels… …improved fan options and compressor plus attenuation options.
  Heating ability… …Heat Recovery option providing usable heat output
Summary:
  New technologies… …offer opportunity for improvement
  No major competitive changes expected… …until next round of efficiency …legislation (2015) EcoDesign.

## Slide 5: YLAA Air Cooled Chiller Product Overview
18 models in range.
Two tier strategy “SE” and “HE”. ….Balance of efficiency, sound and footprint.
All models have two refrigerant circuits. R410A refrigerant Zero ODP! Low GWP!
Multiple 4, 5 or 6 scroll compressors, …enabling a wide operating range around design ….conditions.
Zinc coated Aluminium Micro-channel …condenser ….High efficiency, low charge and pressure drop for ….air flow and sound optimisation.
Direct expansion. 316 Stainless steel. ….High efficiency, low water side pressure drop, brazed …...plate evaporators.
Heavy gauge galvanised steel, baked epoxy power coated, unit frame and control panel.
Unique system optimised JCI controls.
Flexible option packages to address wide range of applications and operational requirements.

## Slide 6: YLAA Air Cooled Chiller Major Product Options
Mechanical:
    HYDROKIT Single Pump or Dual Pump
    Large range also for choice of flow / head requirements. . . ….(no pump option below -7 glycol cooling). …...Standard feature (includes balancing valve, discharge check valve, discharge shutoff …...valve, thermal dispersion flow switch, pressure ports, Y-strainer, bleed and drain valves, and ……frost protection) .......Fully featured (+ service valves, expansion tank port‘s, additional pressor points).
    Ultra quirt fans.
    Compressor Acoustic Enclosure. (With ultra q fans reduce sound by 8dBA)
    Dual Speed Fans (To balance off design sound and efficiency.)
    EC fan for Low Ambient Operation (auto select below -1C ambient).
    High Static Fans 75 Pa (Only above -1C ambient operation for internal application)
    High Air flow fans (For increased cooling performance at high ambient +46C)

## Slide 7: YLAA Air Cooled Chiller Major Product Options
  Design includes a partial condensing brazed plate heat exchanger.
  Amount of heat recovered depends on leaving hot water temperature and operating ambient air temperature.
  Recovery potential is cooling load plus work input
@ 35C ambient
@ 35C ambient
Heat Recovery.

## Slide 8: YLAA Air Cooled Chiller Major Product Options
Electrical:
    Direct on line compressor starting
    Optional Soft Start to reduce maximum inrush current
    Additional Power Factor Correction to 0.9
    Leaving water control temperature remote reset
    Programed or Remote start stop and Common system fault monitoring.
    Building Automation System (BAS) Interface
      (BACnet and MODBUS protocols standard)
    Keypad EPROM documentation available Languages
      English, Spanish, French, German, Italian, Portuguese, Hungarian, Polish
    E coat condenser coil epoxy coated corrosion protection
    Unit / Condenser coil Wire Grill or Louvered Panels

## Slide 9: YLAA Air Cooled Chiller Key Operating Limitations
190 to 518 kW cooling capacity
-12 to 15C leaving evaporator liquid …. (-12C to 5C requires glycol)
-18 to 52C ambient …..(-1C / 46 C standard)
EER up to 3.2
ESEER up to 4.25
Sound Pressure as low as 50 dB(A) … @ 10m (parallel)
    Optional Heat Recovery to 60C
    Electrical power supply 400v 3ph 50 Hz

## Slide 10: YLAA GCSS Selection / Pricing Program and Product Support
    Selection performance effecting options Using selection pick list- Reduced list to speed up selection time
    Selection performance effecting options Using specific unit selection- Note Increased list some options only available within operating limits (soft start, power factor correction below 35C ambient high pressure fans above -1C ambient, no pump selections below -7C leaving chilled liquid, EEV is automatically selected below 5C leaving liquid [SQ for other applications)
    Special Quotation available for non-standard options (Flexibility is currently limited during the production transfer window from Sabadell to Manisa production Please however continue to submit your clients requests for Engineering / Production team review)
    Application support continues through the SQ system

## Slide 11: YLAA Conclusion

## Slide 12
YVAA - YCIV Air-Cooled Screws
Roger Smeed
Notes: 12

## Slide 13
YORK Variable Speed Air-Cooled Screw Chillers A History of Leadership and Innovation
    The global market leader in Variable Speed Drive chillers with 30 years of experience varying compressor motor speeds
Notes: In 2004, we invented the first air-cooled VSD screw chiller. AND NOW, not only do we ship 100% of our air-cooled screw chillers with VSDs, the competition have started to copy us – this is high praise, for sure.
And now, in 2010, we are at it again. We are taking air-cooled screw chiller performance to a whole new level.
30 years experience with V-S-D chillers
  2004 was the first V-S-D air cooled chiller and it was developed by York
Only focus on the third timeline piece…2004

## Slide 14
Proven by Experience
    Over 10 Million kilowatts of VSD, YCAV/YCIV/YVAA/YVWA air-cooled screw chillers operating globally, in more than 100 countries since 2004
    Add together with JCI Large tonnage water cooled centrifugal HT-OT, YT, YK, & YMC2
      Strong installed base in Middle East where harshest outdoor requirements exist (McQuay current limits VSD option over 40ºC)
      Large base in sound sensitive markets like Europe.
    VSD is a standard feature on all YCAV/YCIV and YVAA/YVWA
    All units combined, more than 30,000 years of cumulative field experience
JCI Variable Speed Drive Chiller Experience
Notes: .
This image is copyrighted. JPL needs to build this from the data that Ian/Mike provided. Use the 2010 column as it is the cumulative number for experience for each region
Have 16,000 V-S-D air-cooled screw drive chiller units worldwide
Bottomline: Build great chillers, have the best specs, and the experience that goes along with that

## Slide 15
Product Overview YCIV
YCIV
JCI YORK Second generation Air cooled VSD chiller

## Slide 16: YVAA – YORK Variable Speed Air-Cooled Screw Chillers YCIV Phase Out
  YCIV has been or is now being phased out:
    North America: Phase out complete
    Latin America: Phase out complete
    Asia: Phase out complete
  Europe Middle East and Africa Status:
    YCIV phased out for standard application:
      2-compressor YCIV: Phase out complete March 2012
      3-compressor YCIV: Phase out complete March 2014
    Remains available only for following applications
    Low Temperature (especially Propylene Glycol)
    Heat Recovery
    Fin and Tube Condensers.
    YCIV are on an extended lead time to YVAA

## Slide 17
Product Overview YVAA / YCIV
YVAA
JCI YORK Third generation Air cooled VSD chiller

## Slide 18
Product Overview YVAA Component Layout
Microchannel Condenser Coils
High Efficiency Falling Film Evaporator
Screw Compressor
Microchannel Glycol Cooling Coil

## Slide 19
Product Overview YVAA Component Layout
Oil Separator
High Efficiency Falling Film Evaporator
Economizer Flash Tank
Screw Compressor
Compressor, Oil Separator, Filter Drier & Economizer Tank are Mirror Image on Both Sides of Evaporator

## Slide 20: YVAA – YORK Variable Speed Air-Cooled Screw Chillers New Options
Factory mounted, field configured E-Link option
Suction and filter drier service valve option
New condenser fans options:
High Air Flow
VSD High Air Flow
High Pressure
Sound Optimization
1-pass evaporator option
Single point power supply option on larger units only (standard on smaller models)
Additional box next to VSD Fans panel not shown on picture
Desuperheater
Available on SQ for condenser frame 3 not shown on picture
Glycol Pump
Condenser Fan VSD’s

## Slide 21
    Tailor and Tune
    Full load efficiency
    Part load efficiency
    Full load sound attenuation
    Part load sound reduction
KEY BENEFITS
Notes: As we mentioned at the start of this discussion, YORK invented the first VSD-driven, air-cooled screw chiller in 2004 after years of research and development. Although there are now some other manufacturers offering an option for VSD on air-cooled screw chillers, YORK is still the only manufacturer to make this a standard feature on all air-cooled screw chillers. AND no one else has the engineering and field experience we do in VSD air-cooled screw chillers.
Today, we have over 2 million refrigeration tons (5.2 million kW) of VSD-driven, air-cooled screw chillers operating globally. All units combined, we have more than 18,000 years of cumulative field experience in more than 100 countries.
This image is copyrighted. JPL needs to build this from the data that Ian/Mike provided. Use the 2010 column as it is the cumulative number for experience for each region
Have 16,000 V-S-D air-cooled screw drive chiller units worldwide
Bottomline: Build great chillers, have the best specs, and the experience that goes along with that

## Slide 22
Behind the scenes …
  Typical Chiller Today curve is based on a Class A unit with 3.1 COP
  YVAA can be ‘Tailored & Tuned’ from 2.8 to 3.4 COP
YVAA Configurations
  Various condenser and evaporator sizes can be selected in combination
  Larger heat exchangers yield higher full load efficiency
Falling Film Evaporator and Microchannel Condenser Coils are key to Full Load Efficiency …
Full Load Efficiency
Notes: The YVAA chiller allows you to exceed the ASHRAE 90.1 regulated minimum full load efficiency levels by more than 20%. AND exceed the ASHRAE 90.1 regulated minimum part load efficiencies by more than 50%.
Use the first two main points in content generation.
Not mentioned key: Tailor and Tune. Chiller can be built to spec for capacity and efficiency
Can use the above JCI paragraph to generate content
Design Conditions = Worst Case Scenario
  Occuring 1% of the time of operation but the unit is built to ensure it can handle this
Off Design Conditions = Everyday Operating Scenario
  Occuring 99% of the time of operation
The graph on this slide will need to be on of the images for the content page of brochure
  JCI to provide data to JPL to improve design if needed
ASHRAE:
  An industry engineering group that builds specification for the industry to abide by
    SAE
    AMA
    LEED
    Etc………

## Slide 23
Behind the scenes …
  Typical Chiller Today part load curve is based on a 4.0 ESEER
  YVAA part load is based on an approximately 4.8 ESEER
YVAA Options
  Standard YVAA typical selections have 4.0 – 4.2 ESEER
  Combination of optimized compressor, VSD fans & increased unit frame size allow you to configure any point up to 4.8 ESEER
VSD’s are key to Part Load Efficiency …
Part Load Efficiency
Typical Chiller Today
YVAA
17%
Notes: The YVAA chiller allows you to exceed the ASHRAE 90.1 regulated minimum full load efficiency levels by more than 20%. AND exceed the ASHRAE 90.1 regulated minimum part load efficiencies by more than 50%.
Use the first two main points in content generation.
Not mentioned key: Tailor and Tune. Chiller can be built to spec for capacity and efficiency
Can use the above JCI paragraph to generate content
Design Conditions = Worst Case Scenario
  Occuring 1% of the time of operation but the unit is built to ensure it can handle this
Off Design Conditions = Everyday Operating Scenario
  Occuring 99% of the time of operation
The graph on this slide will need to be on of the images for the content page of brochure
  JCI to provide data to JPL to improve design if needed
ASHRAE:
  An industry engineering group that builds specification for the industry to abide by
    SAE
    AMA
    LEED
    Etc………

## Slide 24
  Just like performance, the YVAA chiller allows you to tailor and tune sound reduction configurations to match your needs
  Flexible selection system allows you to see sound benefit of reduced full load compressor speed (oversize the chiller and slow down the compressors)
  Multiple selection configurations provide ways to offset performance impact of attenuation options
Full Load Sound Attenuation
Notes: Of course, there will always be design considerations that must consider the worst-case noise. Critical property-line sound values can be a controlling factor in placement of air-cooled chillers, or selection of sound attenuation options.
The YVAA chiller can use combinations of enclosures, insulation, and fans options to provide sound reduction to match your sound requirements at design conditions. The unique ability to tailor and tune your configuration provides unmatched flexibility, and applies to sound just as it does other design considerations.
The combination of state-of-the-art sound reduction at design conditions AND the inherent benefits of off-design sound reduction can deliver a perfect fit for almost any application.
This slide to be used for content/copy generation
Bottomline: Tailor and Tune as discussed previously

## Slide 25
Behind the Scenes…
  Typical chiller today is representative of the part load data we have found for chillers with fixed speed screw compressors (gas flow in unloading mechanism is noisy)
  YVAA is a standard unit with staged fan control
  YVAA Optimized adds the impact of VSD
  As the YVAA unloads the compressor with VSD, the fans become the larger noise source unless VSD are also added to the fans
  By combining the two technologies we are achieving performance that most competitor’s cannot offer
Part Load Sound Reduction
YVAA Optimized
YVAA
Typical Chiller Today
Notes: Just as we discussed in regard to energy efficiency, design conditions of capacity and ambient temperature only occur a very small portion of the time a chiller operates. The YVAA chiller, with standard VSD-driven compressors, is unique among air-cooled screw chillers because it provides superior sound reduction as operating conditions become less stringent (lower capacity demand OR lower outdoor ambient temperature).
The hottest, stickiest days are when most neighbors are inside in the comfort of their own air-conditioning system. But on mild days when people are enjoying the outdoors, your chiller operating condition will yield lower sound. On evenings and weekends, when neighbors are more likely to be home and outside, is when sound regulations are the tightest – it is precisely these times when the benefit of lower cooling capacity demand and lower ambient temperatures are most likely to occur. And the addition of VSD drive to the condenser fans only multiplies the benefit you get in part load sound reduction.
The only thing better than having part load sound reduction, is the ability to put it in your control. The SilentNight feature provides ‘night setback’ for the neighborhood. SilentNight offers you BAS or programmable control to limit the chiller load and make sound your priority. This can be especially effective when changes in sound regulations are triggered by specific times of day.
All together, this makes the YVAA chiller a perfect fit for when quiet operation can make you a good neighbor.
SilentNight
  This is a York/JCI term for load shedding or using the Building Automated System to artificially reduce the unit output to match sound specs for certain time mandated by government and surroundings
V-S-D will be extremely benifiical in controlling sound by allowing the compressor to run at reduced load during those off design conditions when sound regulations are tightest, evenings and weekends.
JCI will provide the graph data to JPL to enhance it visually

## Slide 26: YVAA – YORK Variable Speed Air-Cooled Screw Chillers Configuration up to 1,660 kW released in August 2013
  4 new configurations
    YVAA 1343, YVAA1443, YVAA1315, YVAA1700
    All using 2 compressors only
    Fit for containerization (40ft) / road freight
    Dual point power supply as standard (Single point available as an option)
  New set of options

## Slide 27: YVAA – YORK Variable Speed Air-Cooled Screw Chillers Larger configurations to 1,750kW planned for FY15 release
  Capacity, efficiency increases – containers do not
  YVAA provides maximum capacity in 20’ and 40’ container (frame size YVAA0700 and YVAA1700)
  Large units designed to split
    Units designed to fit in 40’ + 20’ container
    Road transportation / Sea freight restrictions on larger units
    Full refrigerant charge contained in primary section
    Field connections via flange and plug – no wiring, no brazing
Design is complete, pending receipt of final PED/CE certificates to release

## Slide 28: YVAA – YORK Variable Speed Air-Cooled Screw Chillers New Option – Quick Restart
  Quick Restart option reduces the time to full load after a power failure
  Quick Restart option to be offered to application meet the following criteria:
    High cooling load year round
    Value of “Time to full load” is high
    Cooling serving business critical processes
    Target Application: Data Centers, Industrial process cooling
  Quick Restart customer benefits:
    Rapidly re-establishes chilled water temperature
    Keeps process equipment cooled / process on.
    Reduces the chance of very expensive downtime
    Reduces or eliminates buffer tanks or thermal storage systems

## Slide 29: YVAA – YORK Variable Speed Air-Cooled Screw Chillers New Option – Quick Restart
Standard YVAA – Time to full load: 8-9 minutes – 50% better than average
Quick Start YVAA – Time to full load: 4-5 minutes – 4 times better than industry average
  Compressors start in 30 seconds instead of normal 2 minutes
VSD technology enables both compressors to start simultaneously.
High cooling load enables us load the chiller faster than normal without risk of overshooting to shutdown conditions
Reducing the anti-recycle timer from 2 min to 30 sec

## Slide 30: YVAA – YORK Variable Speed Air-Cooled Screw Chillers New Option – Quick Restart – Simulated Power Failure
Cooling Capacity (TR)
Unit Current (Amps)
Temperature (deg F)
Cooling Capacity
Leaving Water Temp.
Return Water Temp.
Unit Current
10:56:00
Power Failure
10:56:30
Unit restarts
10:59:00
Unit back to full load
Time to full load: 3 min

## Slide 31: Monterrey Witness Test Facility Update

## Slide 32: YVAA – YORK Variable Speed Air-Cooled Screw Chillers Monterrey Witness Test Laboratory
  Test Lab. dedicated to customer witness tests
  Opened Q3 2014 Demonstrated 4 Successful European tests
    Designed for full load testing up to 1,750 kW; both 50 and 60 Hz
    Full load, part load, sound testing
    System safeties.
    AHRI & Eurovent certified laboratory
    Global test facility serving our customers across the Globe
    There will be Video conferencing capabilities from key JCI offices
      Brussels, YORK Pa, Milwaukee,…
  Only Limited test slots allocated by region !!!
    Highest risk: Overbooking the test lab
    Key to success: balancing demand with lab. capacity
Process to quote is through the SQ data base need
Detail of all tests required, + Equipment data sheet, part load report

## Slide 33: YVAA – YORK Variable Speed Air-Cooled Screw Chillers YVAA Eurovent and AHRI Certifications
  Eurovent Certification:
      This labority has allowed JCI to increase Eurovent certified models from our 2013 limit certify all models below 600 kW.
      YVAA will participate into the voluntary certification program (600 kW – 1,500 kW)
      YVAA up to 1,500 kW will be Eurovent certified
  AHRI Certification:
    Both 60 Hz and 50 Hz configurations are certified
    YORKworks is AHRI certified
Eurovent and AHRI certification validates performance without need for customer testing. Specify performance certification first!

## Slide 34: Competitive Landscape Update

## Slide 35: YVAA – YORK Variable Speed Air-Cooled Screw Chillers Trane RTAE – Overview
  Trane RTAE “Stealth” Chiller
    Released to Europe in June 2014
    Currently only available in 50Hz configurations
    Capacity range: 500-1000 kW
    8 fixed capacity models
  Notable Features
    Screw compressor technology “optimized for VSD operation”
    “24-pulse” Adaptive Frequency Drive (AFD3)
    “All Aluminum” condenser coils
    “Permanent magnet” fan motors
    “InviSound Superior” and “InviSound Ultimate” sound reduction package

## Slide 36: YVAA – YORK Variable Speed Air-Cooled Screw Chillers Trane RTAE – What do we know so far?
  Screw compressor technology “optimized for VSD operation”
    Unlike other competitors, VSD is standard on RTAE (not an add-on option)
    2 compressors operated at 4 different frequencies giving 8 models in total
    Permanent magnet motors claimed to improve efficiency by 4%….more later
    Same technology as ours…9 years later
  “24-pulse” Adaptive Frequency Drive (AFD3)
    Sales Brochure and Press Release are highlighting the use of a 24-pulse VFD.
    RTAE based specification calling for 30% TDD and use of line reactor
      Typical characteristics of a 6-pulse drive
      YVAA complies
    Strong indication that “24-pulse” drive is an option
      24-pulse VFD typically costs around 3 to 4 times the cost of 6-pulse drive
      Would represent around 50% add-on cost option

## Slide 37: YVAA – YORK Variable Speed Air-Cooled Screw Chillers Trane RTAE – What do we know so far?
  “Permanent magnet” variable speed fan motors
    Sales Brochure and Press Release are highlighting the use of permanent magnet, variable speed fan motors.
    RTAE based specification calling for direct drive condenser fans
    Permanent magnet motor claimed to increase efficiency at part load 5% or more….more later
    Strong indication that fixed speed fans as standard and VSD fans as an option
  “All Aluminum” condenser coils
    3-row coil with aluminum tubes and fins arrangement – NOT Microchannel
    RTAE based specification calling for copper tubes and aluminum fins coils
    “All Aluminum” condenser coils appears to be an option to bid on specification calling for MCHX
    “The tubing is a long life alloy designed to deliver corrosion performance that meets or exceeds Microchannel coils.” (Extract from RTAE Engineering Guide)

## Slide 38: YVAA – YORK Variable Speed Air-Cooled Screw Chillers Trane RTAE – What do we know so far?
  “InviSound Superior” and “InviSound Ultimate” sound reduction packages
    InviSound Superior: 99 dB(A) at 1000 kW. Easily matched with YVAA
    InviSound Ultimate: 92 dB(A) at 1000 kW. YVAA can do 94 dB(A) at the same capacity
      Includes fan rotation speed reduction to 60% of nominal value
        Typically equates to 10-15% reduction in efficiency (dropping 2 Eurovent class)
      Includes purpose built, pressed metal and acoustic lining compressor enclosure
        Appears to be an expensive option
  Limited Operating Range as standard
    Standard Ambient Range: 0ºC to 40.6ºC
    Low Ambient Range: -17.7ºC to 40.6ºC (additional control logic and sensors)
    High Ambient Range: 0ºC to 52ºC (larger compressor motors and larger drive)
    Force high cost on RTAE by specifying capability to operate in ambient conditions below 0ºC and above 40.6ºC

## Slide 39: YVAA – YORK Variable Speed Air-Cooled Screw Chillers Trane RTAE Vs YORK YVAA – Head to Head Comparison
 | RTAE 165 | YVAA0665 | 
Cooling Capacity | 570 kW | 570 kW | =
Input Power | 167 kW | 174.5 kW | û
Full Load Efficiency | 11.6 EER | 11.10 EER | û
NPLV | 18.7 | 19.1 | ü
Sound Pressure (at 30ft) | 70 dBA | 70 dBA | =
Water Pressure Drop | 36.4 ft H20 | 31.1 ft H20 | üü
Length | 283.7 in | 291.7 in | ü
Minimum Load | 19% | 10% | ü
Operating Conditions:
Chilled liquid: 13.8ºC/ 7.2ºC 35 % PG
Ambient temperature: 35ºC
Power Input: 400V / 3 ph. / 50 Hz
Trane Website:
“Trane® Stealth™ air-cooled chillers deliver the highest combination of part-load and full-load efficiencies and the lowest published sound levels. No other air-cooled chiller can match this kind of efficiency or sound performance.”

## Slide 40: YVAA Competitive Landscape Update

## Slide 41
30XA
RTAC
FOCS
AWS
YCIV
YVAA
YVAA – YORK Variable Speed Air-Cooled Screw Chillers
Competitive Landscape

## Slide 42
FOCS
Screw, variable speed standard | Screw, fixed speed | Screw, fixed speed | Screw, fixed speed | Screw, fixed speed
Micro channel, all aluminum | Traditional, copper tubes aluminum fins | Micro channel (optional copper tubes aluminum fins) | Traditional, copper tubes aluminum fins | Traditional, copper tubes aluminum fins
Totally Enclosed, Air Over (TEAO) | Standard: Open Drip Proof (ODP) Option: TEAO | Totally Enclosed, Air Over (TEAO) | Totally Enclosed, Air Over (TEAO) | Totally Enclosed, Air Over (TEAO)
Falling film | Falling film | Fully flooded | DX | DX
YVAA – YORK Variable Speed Air-Cooled Screw Chillers
Competitive benchmarking - Components
Above Average
Average
Below Average

## Slide 43
FOCS
1 compressor per circuit | 2 compressors for 1 circuit for models with 3 and 4 compressors | 1 compressor per circuit | 1 compressor per circuit | 1 compressor per circuit
10% | 15% | 15% | 2 compressors: 15% without VSD 20% with VSD 3 compressors: 8% without VSD 13% with VSD | 2 Compressors stepped 25% 3 compressors stepped 17% 4 Compressors stepped 13%
R134a Low quantity | R134a High quantity | R134a Low quantity | R134a Medium quantity | R134a Medium quantity
YVAA – YORK Variable Speed Air-Cooled Screw Chillers
Competitive benchmarking - Components
Above Average
Average
Below Average

## Slide 44
FOCS
Tailor and tune | Standard and High | High | Standard, High, and Premium | Standard, High, and Premium
Tailor and tune | Standard | High | Standard, High, and Premium | Standard, High,
Low at full load Very low at part load | Medium | Low | Very low | Medium and Low
YVAA – YORK Variable Speed Air-Cooled Screw Chillers
Competitive benchmarking - Performance
Above Average
Average
Below Average

## Slide 45
FOCS
Low | Very high | Low | Medium | Low
Small to medium | Very small | Medium | Medium to large | Medium
Standard: 0F to 125F (-18C to 52C) | Standard: 25F to 115F (-4C to 46C) | Standard: 0F to 115F (-18C to 46C) | Standard: 35F to 100F (2C to 38C) | Standard: 0F to 115F (-18C to 46C)
 | Options: Low ambient of to 25F (-18C to -4C) High ambient 115F to 125F (46C to 52C) | Options: High ambient 115F to 125F (46C to 52C) | Options: Low ambient 0F to 35F (-18C to 2C) High ambient 105F to 125F (40C to 52C) | Low Ambient -15C High ambient 46C
YVAA – YORK Variable Speed Air-Cooled Screw Chillers
Competitive benchmarking – Physical Attributes
Above Average
Average
Below Average

## Slide 46
FOCS
Standard: VSD with no inrush current | Standard: Across-the-line | Standard: Wye-delta | Standard: Solid state | Part Wind
 | Option: Wye-delta | Options: Across-the-line Non-fused disconnect | Options: Wye-delta VSD | Options: Wye-delta VSD
Standard: Single point power | 2 compressors: Standard: Single point power Option: Dual point power 3 or 4 compressors: Standard: Dual point power Option: Single point power | Up to 350 tons (1200 KW): Single point power Higher than 350 tons (1200 KW): Dual point power | Standard: Multi-point power with 1 disconnect switch per circuit (2 point for 2 compressors, 3 point for 3 compressors) No compressor breakers Option: Single point power | 2 compressor single point 3 & 4 Compressor dual point
YVAA – YORK Variable Speed Air-Cooled Screw Chillers
Competitive benchmarking - Electrical
Above Average
Average
Below Average

## Slide 47: YVAA GCSS Selection Program

## Slide 48
YVWA and GCSS
YVAA is a Taylor and tune product family, providing many varied solutions to the specific conditions requested by your client.
There is a need for you to understand how our selection tool works so you can provide your client with the optimum selections(s)
As with the YLAA there are options that effect the unit performance and we recommend you review and deselect those which are not suitable for your project.
Compressor part load efficiency, Fan selection, Acoustic insulation.

## Slide 49
YVWA and GCSS
For extreme low sound applications we also offer the
Optimised Sound optional program
For this selection please select the following performance effecting options
Both low and ultra low VSD fan options (only)
Both Standard and Optimised Compressors
Both sound kits 1 and 2.
Add the lowest acceptable EER

## Slide 50
The Optimised Sound optional program
Looks to identify the balance point between the fan and compressor sound levels / speeds to meet the requested cooling capacity and minimum gross EER.
This is achieved by balancing the operating speeds of fan and compressor (+ acoustic insulation) so that neither element is dominant.
This option has reduced unit sound levels by up to 7dBA for a relative low price addition, compared to alternate acoustic solutions
YVWA and GCSS

## Slide 51: New Collaterals

## Slide 52: YVAA – YORK Variable Speed Air-Cooled Screw Chillers New Collaterals
  “A chiller as unique as your data center”
    Centered on data center applications
    Walks through YVAA value proposition to data center customers
    Energy efficiency, VSD technology, Quick Re-Start, Confidence
  “Microchannel Review”
    Review MCHX challenges specific to stationary HVAC applications
    Explain JCI technology choices and qualification process
    Good complement to the Microchannel technology white paper.
  Chiller Solutions – Competitive Database Portal
    New portal concentrating our Chiller competitive intelligence
    First phase focused on YVAA
    More details during tomorrow’s session

## Slide 53
Johnson Controls
Questions?